## Sheet1
Question | Answer
1. Under which severe weather conditions is it strictly prohibited to install or operate outdoor equipment and cables for the EB-L-3.2K battery? 2. What are some strictly forbidden actions when handling, maintaining, or operating the EB-L-3.2K battery according to its safety warnings? 3. What immediate actions must be taken if a fire occurs involving the EB-L-3.2K battery? 4. What general safety principles must be followed when operating the EB-L-3.2K battery to prevent electric shock, fire, or serious injury? | This is a EB-L-3.2K battery. The equipment has a high voltage. Irregular operation may generate electricshock or fire which may cause death, severe personal injuries or serious property damages. Please standardize the operation： ● It is strictly prohibited to install or operate outdoor equipments and cables (including handling equipment, operating equipment and cables, plugging and unplugging signal interfafaces connected to theoutdoors, working at heights, outdoor installation, etc.) in severe weather such as thunderstorm, snowy weather, strong breeze. ● Please observe the operation sequence and safety precautions in this manual and other related manuals. ● Follow the warning signs, cautions and precautions on the equipment. ● Follow the manual to use correct tools, and master the correct use of tools. ● Do not install and connect cables, maintain, or replace equipments with power on. ● Do not wash the equipment. ● Do not open the panel of the equipment. ● Measure the voltage before touching conductor surface or terminal to verify that there is no risk of electric shock. ● Repair the scratches that occur during equipment transportation and installation in time. It is strictly forbidden to expose the scratched parts to the outdoor environment fofor a long time. ● It is forbidden to lift ft and transport the batteries through the battery terminals or bolts. ● Do not alter the internal structure or installation procedure of the equipment without prior permission of the manufacturer. ● Leave the building or the equipment area and turn on the fire alarm or make an emergency call immediately in the case of a fire. Do not enter the building on fire in any case.
1. Who is permitted to install, operate, and maintain the EB-L-3.2K battery? 2. Who has the authorization to remove security facilities and overhaul the EB-L-3.2K equipment? 3. Which personnel categories are qualified to replace equipment or components (including software) for the EB-L-3.2K? 4. How does the EB-L-3.2K manual differentiate between "Professionals" and "Trained Personnel"? 5. What qualifications must personnel handling high-voltage operations for the EB-L-3.2K possess? | This is a EB-L-3.2K battery. There are some personnel requirements you should obey： ● Personnel installing or maintaining EnValt equipment must be trained, understand all necessary safety precautions, and be able to correctly perform all operations. Personnel who will operate the equipment, including operators, trained personnel and professionals should possess local national required qualifications in special operations such as high-voltage operations and operations of special equipment. ● Only qualified professionals or trained personnel are allowed to install, operate and maintain theequipment. ● Only qualified professionals are allowed to remove security ty facilities and overhaul equipment. ● Only professionals or authorized personnel are allowed to replace the equipment or components(including software). Professionals: personnel who are trained or experienced in equipment operations and are clear of thesources and degree of various potential hazards in equipment installation, operation and maintenance. Trained personnel: personnel who are technically trained, have required experience, are aware of possible hazards on themselves in certain operations and are able to take protective measures to minimize the hazards on themselves and other people. Operators: operation personnel who may come into contact with the equipment, except trained personnel and professionals.
1. What are the basic environmental requirements for installing the EB-L-3.2K battery? 2. Where should the EB-L-3.2K battery be installed in a garage to ensure safety? 3. What special precautions should be taken when installing the EB-L-3.2K battery in a basement? 4. Why should the EB-L-3.2K battery be kept away from water sources during installation? 5. In what types of locations is it prohibited to install the EB-L-3.2K battery? | This is a EB-L-3.2K battery. There are some installation environment requirements you should obey: ● The installation and operating environment must comply with international, national and local standards fofor lithium batteries and with local laws and regulations. ● Install in a location out of the reach of children. ● Garage installation needs to be far away frfrom the direction of vehicle travel, it is recommended to install the energy storage on the wall above the body bumper to avoid an accidental collision. ● When installing the battery in a basement, keep good ventilation. Do not place flammable or explosivematerials around the battery. It is recommended that the battery be mounted on the wall to avoid contacting with water. ● Install the battery in a dry and well-ventilated environment. Secure the battery on a solid and flat surface. ● Install the battery in a sheltered place or install an awning over it to avoid direct sunlight or rain. ● Install the battery in a clean environment that is free from sources of strong infrared radiation, organicsolvents, and corrosive gases. ● Precautions should be taken for installation in areas with frequent natural disasters such as floods, mudslides, earthquakes and typhoons. ● Keep the battery away from fire sources. Do not place any flammable or explosive materials around the battery. ● Keep the battery away from water sources such as taps, sewer pipes, and sprinklers to prevent water seepage. ● Do not install the battery in a position where it is easy to touch as the temperature of the chassis andheat sink is high when the battery is running. ● To prevent fire due to high temperature, ensure that the vents and the cooling system are not blockedwhen the battery is running. ● Do not expose the battery to flammable, explosive gas or smoke. Do not perfoform any operation on thebattery in such an environment. ● Do not install the battery on a moving object, such as ship, train or car. ● Do not install the system outdoors in a salt-affected area because the system may be corroded. A salt- affected area is an area within 500m from the coast or affected by sea breeze. The area affected by the seabreeze varies according to meteorological conditions (such as typhoons and seasonal winds) or topographical conditions (such as DAMS and hills).
1. What general electrical safety precautions should be taken before connecting cables to the EB-L-3.2K battery? 2. What are the specific DC operation safety requirements when working with the EB-L-3.2K battery? 3. What temperature-related precautions must be followed when routing cables for the EB-L-3.2K battery? 4. How should cables be handled for the EB-L-3.2K battery when working in low temperature environments? 5. What are the proper procedures for connecting and disconnecting power cables on the EB-L-3.2K battery? | This is a EB-L-3.2K battery. There are some electrical requirements you should obey: 1. For generaral requirerements: Before connecting cables, ensure that the product is intact. Otherwise, electric shocks or fire may occur. Ensure that all electrical connections comply with local electricalstandards. Ensure that the cables you prepared meet local regulations. Use dedicated insulated tools when performing high-voltageoperations. 2. For DC operation: Do not connect or disconnect power cables with power-on. Transient contact between the core of the power cable and the conductor will generate electric arcs or sparks,which may cause fire or personal injury. Before connecting cables, cut off the power supply if people may ccontact energized components Please ensure that the label on the power cable is correct before connecting the power cord Disconnect all inputs and operate the equipment only after the equipment is powered off. 3. For cabling requirements: When routing cables, ensure that a distance of at least 30mim exists between the cables and heat-generating components or areas. This prevents damage of the insulation layer of the cables. When the temperature is low, violent impact or vibration may damage the plastic cable sheathing. To ensure safety, comply with the following requirements: Cables can be laid or installed only when the temperature is higherthan 0°C. Handle cables with caution, especially at a low temperature. If the storage environment temperature of the cables is below 0°C, the cables must be stored at room temperature for more than 24 hours before laying the cables.
1. What personal protective equipment is required when operating the EB-L-3.2K battery? 2. What safety precautions should be taken regarding the temperature of the EB-L-3.2K battery during operation? 3. What are the specific handling requirements for the electrolyte in the EB-L-3.2K battery? 4. What are the prohibited actions when working with the EB-L-3.2K battery to prevent electrical hazards? 5. What safety measures should be followed when connecting or disconnecting the EB-L-3.2K battery terminals? | This is a EB-L-3.2K battery. For personal safety, wear proper personal protective equipment during operation If there is a probability of personal injury or equipment damage, stop the operations and take feasible proteective measures immediately ● Use tools correctly to avoid hurting people or damaging the equuipment. ● The anti-static gloves must be worn when touching the equipment. Do not wear clothes that can easily generate static electricity. ● Do not touch the shell when the equipment is running, the temperature of the shell is high, which may cause burns. ● To ensure personal safety and normal use, it should be grounded reliably before use. ● When the battery is faulty, the temperature may exceed the burnthreshold of the touchable surface. Therefore, avoid touching the battery. ● The electrolyte is harmful to your skin and eyes, so do notdisassemble or damage the battery and avoid contact with the electrolyte. ● Do not place irrelevant objects on the top of the equipmient or insert them into any position of the equipment. ● Do not place flammable objects around the equipment. ● To prevent explosions and body injuries, do not place batterries in a fire. ● Do not place the battery module in water or other liquids. ● Do not short-circuit the battery terminals or it will cause afire ● Do not use water to clean electrical components inside or outside ofa cabinet. ● Do not stand,rely or sit on the equipment. ● Do not destroy any module of the equipment. ● Batteries may cause electric shocks and high short-circuit currents. When using the battery, pay attention to the following points: a) Remove all metal objects from yourself, such as watches and rings. b) Use tools with insulated handles. c) Wear rubber gloves and boots.. d) Do not put tools or metal parts on the top of the battery. e) Disconnect the charging power supply before connecting ofr disconnecting the battery terminal. f) Determine if the battery is unexpectedly grounded. Please renmove power from the ground if accidental grounding occurs.
1. What environmental conditions should be avoided to prevent overheating and fire hazards for the EB-L-3.2K battery? 2. How should the EB-L-3.2K battery be stored to minimize safety risks? 3. What are the specific fire and chemical hazards associated with the lithium-ion battery in the EB-L-3.2K system? 4. Why must damaged EB-L-3.2K batteries not be used or stored near undamaged products? 5. What activities are prohibited around the EB-L-3.2K battery to avoid potential ignition sources? | This is a EB-L-3.2K battery. For battery safety, do not expose batteries at high temperatures or aroundI heat-generating sources, such as sunlight, fire sources, transformers and heaters. The battery may cause afire if overheated. ● To avoid leakage, overheating or fire, do not disassemble, alIter or damage batteries, do not insert foreign objects into batteries or place batteries in water or other lioquids ● The fire hazard of the lithium-ion battery energy storage systemis high. Consider the following safety risks before handling batteries: 1. Battery electrolytes can be combustible, toxic and volatile. 2. Battery thermal runaway can generate flammable gas and harmfulgas such as CO and HF. 3. The excessive concentration of flammable gas generated from Ibattery thermal runaway may cause combustion and explosion. ● The batteries must be stored separately inside the packagirig. Do not store batteries together with other materials or in the open air. Do not stack batteries too high ● Do not use batteries beyond the warranty period. ● Do not remove the battery packaging before use. Batteries should be charged during storage by professionals as required. Put batteries back into their packaging affter charging during storage ● Move batteries in the correct direction. Do not place a battery upside down or tilt it. ● Protect batteries from impact. ● Do not perform welding or grinding work around batteries toprevent fire caused by electric sparks or arcs. ● Use batteries within the temperature range specified in this maanual. ● Do not use damaged batteries (such as damages caused whena battery is dropped, bumped or dented on the enclosure). Damaged batteries may release flammablegases. ● Do not store damaged batteries near undamaged products. ● Do not place damaged batteries in close proximity to flammable materials. ● Monitor damaged batteries during storage for signs of smoke,flammable electrolyte leakage, or heat.
1. What should be done if the EB-L-3.2K battery is damaged or flooded? 2. How should you handle a EB-L-3.2K battery that has been wet or immersed in water? 3. What precautions should be taken when dealing with a leaking EB-L-3.2K battery? 4. What personal protective equipment is required for professionals handling a damaged EB-L-3.2K battery? 5. What first aid measures should be taken if someone comes into contact with the electrolyte from a EB-L-3.2K battery? | This is a EB-L-3.2K battery. For damagaged battery: ● If the battery is damaged or flooded, it may leak the electrolyte andcause a short circuit fire ● If the battery is wet or immersed in the water, do not try to toudth it. ● If the battery seems to be damaged, they are not suitable for use and may be dangerous to personals or property. ● Avoid touching the leaked liquids or gases in the case of batteryleakage or abnormal odor, do not approach the battery and contact professionals immediately. P1rofessionals must wear safety goggles, rubber gloves, gas masks, and protective clothing. ● Electrolyte is corrosive and can cause irritation and chemicalburns. In case of direct contact with the battery electrolyte, do as follows: 1. Inhalation: Evacuate contaminated areas, get fresh air imrmediately and seek immediate medical attention. 2. Eye contact: Immediately flush your eyes with water for at least 15 minutes, do not rub your eyes and seek medical attention immediately. 3. Skin contact: Wash the affected areas immediately with soapand water and seek medical attention immediately. 4. Ingestion: Seek immediate medical assistance.
1. What should be done if the EB-L-3.2K battery is dropped during installation? 2. What emergency measures should be taken if a dropped EB-L-3.2K battery shows damage, odor, smoke or fire? 3. How should a dropped EB-L-3.2K battery be handled if there is no visible damage or abnormalities? 4. What are the potential safety risks of using a EB-L-3.2K battery that has been dropped or impacted? 5. Who should be contacted for proper disposal of a dropped EB-L-3.2K battery? | This is a EB-L-3.2K battery. About battery drop emergency measures: ● If a battery is dropped or violently impacted during installation, iinternal damage may occur. Do not use such batteries. Otherwise, safety risks such as cell leakage and eleectric shock may arise. ● If a dropped battery has obvious damage or abnormal odor, smoke or fire occurs, evacuate the personnel immediately, call emergency services, and contact professionals. Professionals can use fire extinguishing facilities to extinguish the fire under safety protection. ● If a dropped battery has no obvious deformation or damage and rno abnormal odor, smoke or fire occurs, contact professionals to transfer the battery to an open and safe place or contact a recycling company for disposal.
1. What should be the first step when dealing with a fire involving the EB-L-3.2K battery? 2. What types of fire extinguishers are recommended for putting out fires in the EB-L-3.2K battery? 3. What safety precaution should firefighters take when extinguishing a fire in the EB-L-3.2K battery system? 4. What hazards may occur if the EB-L-3.2K battery overheats during a fire? 5. Why should people keep away from the EB-L-3.2K battery during a fire emergency? | This is a EB-L-3.2K battery. For fire emergency measures: ● If a fire occurs, power off the system if it is safe to do so. ● Use carbon dioxide, FM-200 or ABC dry powder extinguishers to extinguish the fire. ● Ask firefighters to avoid contacting with high-voltage componerthe during extinguishing fires to prevent the risk of electric shock. ● Overheating may cause batteries to deform and leak corrosive electrolyte or toxic gas. Keep away from the batteries to avoid skin irritation and chemical burns.
1. How should used EB-L-3.2K batteries be disposed of according to regulations? 2. What should be done if the EB-L-3.2K battery leaks or gets damaged? 3. Who should be contacted when the EB-L-3.2K battery reaches the end of its service life? 4. What environmental conditions should be avoided when storing EB-L-3.2K batteries for disposal? 5. Why can't EB-L-3.2K batteries be treated as household waste during disposal? | This is a EB-L-3.2K battery. For battery recovery process: ● Dispose of used batteries in accordance with local laws andregulations. Do not dispose of batteries as household waste. ● If the batteries leak or are damaged, contact technical suppport or a battery recycling company for disposal. ● If the batteries are out of service life, contact a battery recycling company for disposal. ● Do not expose batteries to high temperatures or direct sunliglnt. ● Do not expose batteries to high humidity or corrosive environments
1. What are the key features and benefits of the EB-L-3.2K home energy storage system? 2. What type of battery technology is used in the EB-L-3.2K system and what advantages does it offer? 3. What is the nominal current rating for the EB-L-3.2K battery and what precautions should be taken regarding current limits? 4. What additional equipment is required when connecting the EB-L-3.2K to an inverter with current exceeding 60A? 5. What functional capabilities does the modular design of the EB-L-3.2K system provide? | This is a EB-L-3.2K battery which is a new generation equipment with home energy storage system that can meet the diverse needs of global users. High-performance lithium iroin phosphate battery is used for functional integration and modular structure design. It has realizedthe convenient expansion, rapid product installation, load matching, remote control and many other functions Notes : The nominal current of the EB-L-3.2K productis 60 A. Please do not operate it under conditions exceeding this current. If the input or output current of the inverter connected to the battery exceeds 60 A, please use it in conjunction with the EnValt compiner box.
1. What are the main components of the EB-L-3.2K battery system? 2. What type of battery cell is used in the EB-L-3.2K system? 3. What is the function of the BMS in the EB-L-3.2K battery system? 4. How does the BMS contribute to the safety of the EB-L-3.2K battery? 5. What are the primary responsibilities of the BMS in managing the EB-L-3.2K battery? | This is a EB-L-3.2K battery. About system composition, the battery system consists of BMS and battery. The battery consists of a high-performance lithium iron phosphate cell that can be charged and discharged to the load. BMS(Battery Management System) is an intelligent electronic system that manages the charge and discharge of batteries and provides system safety protection.
1. What does "HOME - ESS" represent in the EB-L-3.2K battery model? 2. What is the meaning of "LV" in the EB-L-3.2K battery model? 3. What does "3.2K" indicate in the EB-L-3.2K battery model? 4. How is the model name EB-L-3.2K structured and what does each part mean? 5. Where can one access detailed information about model identification description of the EB-L-3.2K battery model? | This is a EB-L-3.2K battery. About model identification description, the name is split into three parts: "HOME - ESS" , "LV" , and "3.2K" . HOME - ESS refers to Product, which means Home energy storage. LV refers to Voltage strength, which means Low Voltage. 3.2 K refers to Battery sizes, which means The battery capacity is 3.2kW·h. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623144924034.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623144950700.png
1. What are dimension and weight the EB-L-3.2K battery model? 2. Where can one access detailed information about the product dimension and weight of EB-L-3.2K battery model? | This is a EB-L-3.2K battery. About product dimension and weight, width is 484mm, depth is 165mm, height is 302mm and weight is 34.9kg The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623145304264.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623145315160.png
1. Where is the CAN port located on the EB-L-3.2K battery as per the interface location chart? 2. What is the position of the RS485-IN port on the EB-L-3.2K battery's interface location diagram? 3. In the interface location chart of the EB-L-3.2K battery, where can the RS485-OUT port be found? 4. According to the given interface location chart, where is the DIP switch located on the EB-L-3.2K battery? 5. Where is the RESET port located on the EB-L-3.2K battery from the provided interface location diagram? 6. Give me a technical diagram of interface location chart of EB-L-3.2K battery. | This is a EB-L-3.2K battery. The link below provides a technical diagram of interface location chart. In the diagram, various ports are labeled such as CAN, RS485-IN, RS485-OUT, DIP, and RESET, along with positive (+) and negative (-) connections. There is a main device in the center and a separate WIFI module indicated to its right. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623145706221.png
1. Give me a diagram of symbol explanation of EB-L-3.2K battery. | This is a EB-L-3.2K battery. There are some symbol explanation in the link below: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623150358616.png
1. Give me a diagram of product parameters of EB-L-3.2K battery. 2. What does Models / Dimensions (mm) / Enclosure protection rating / Module configuration / Nominal voltage (V) / Operating voltage range (V) / Nominal Energy (Wh) / Nominal discharge current (A) / Max. discharge current (A) / Nominal charge current (A) / Max. charge current (A) / Charge temperature range (°C) / Discharge temperature range (°C) / Total weight (Kg) / Communication interface / Maximum parallel number means in EB-L-3.2K battery | This is a EB-L-3.2K battery. About product parameters, the table of project, paramater and remark are listed in belew: 1. Models: EB-L-3.2K 2. Dimensions (mm): W*D*H 484*165*302 3.Enclosure protection rating: IP54 4 Module configuration: 1 parallel 16 strings (1P16S) 5 Nominal voltage (V): 51.2 6. Operating voltage range (V): 43.2~57.6 7. Nominal Energy (Wh): 3225.6 8. Nominal discharge current (A): 60 9. Max. discharge current (A): 65 10. Nominal charge current (A): 40 11. Max. charge current (A): 65 12. Charge temperature range (°C): 0~50 13. Discharge temperature range (°C): -10~50 14. Total weight (Kg): 34.9 15. Communication interface: CAN/RS485/WIFI/Bluetooth 16. Maximum parallel number: 16 The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623151422517.png
1. What qualifications should product installers have to install the EB-L-3.2K battery? 2. What aspects of electrical equipment should installers of the EB-L-3.2K battery be familiar with? 3. What are the capabilities that installers of the EB-L-3.2K battery should possess regarding electrical equipment operation? 4. In terms of protective tools for electrical equipment of the EB-L-3.2K battery, what should installers know how to do? | This is a EB-L-3.2K battery. About personnel qualification to install the battery, product installers should have received safety technical training, olbtained the local electrician certifications and the authorized qualifications for product installation. And insstallers should be familiar with electrical equipment, accumulate relevant experience and have the follovving capabilities, including but not limited to: ● Setup, startup, shutdown, grounding, short-circuiting and repair ofelectrical equipment. ● Standardized maintenance and use of protective tools for electricalequipment. ● Providing emergency assistance for the injured. ● Complying with local laws, regulations, standards and directivees.
"1. What is the installation environment of the EB-L-3.2K battery? 2. Give me a diagram of the installation environment of the EB-L-3.2K battery?" | This is a EB-L-3.2K battery. About installation environment, Please make sure the installation location meets the followingg conditions: ● The building is designed to withstand earthquakes. ● The floor is flat and hard, and the area has minimal dust anddirt ● The ambient environment is cool, dry, well-ventilated, and avway from the sea, salt water, humid air, heat sources as well as direct sunlight. ● Temperature and humidity are kept at a constant level. ● There are no flammable and explosive items, corrosive gases, including ammonia and acid vapors, and contaminants. Note: If the ambient temperature exceeds the operating rangge, the battery will stop working to protect itself. The optimal temperature range for battery operation is 15°C to 35°C. Frequent exposure to inappropriate temperature may reduce battery performance and life. When the installation environment of the system does not meet the above shading requirements, users can choose to use the EnValt outdoor box in combination with the system, or build an installation environment that meets the conditions on their own. Note: Please install the system and outdoor box according to the operating requirements. Otherwise, EnValt will not be liable for any warranty claims resulting from system damage. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250711091852656.png
1. What is the installation angel of the EB-L-3.2K battery? 2. Give me a diagram of the installation angel of the EB-L-3.2K battery? | This is a EB-L-3.2K battery. About installation angel, the battery can be installed on the ground or the wall. When the battery is installed on a wall, install it on a flat wall and keep the battery parallel to the wall. And don't install the battery at inclined, horizontal,or upside down positions. Below is the link of sample of installation angel. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623153216314.png
1. What is the installation space of the EB-L-3.2K battery? 2. Give me a diagram of the installation space of the EB-L-3.2K battery? | This is a EB-L-3.2K battery. For installation space, leave enough space to install the battery. When the battery is mounted on a wall, do not place any objects under the battery. At least 300 mm of space should be left around each unit and the vertical distance between them should be in the range of 0.4 m - 10 m. Installation space diagram as shown below. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623154140778.png
1. What personal protective equipment is required when installing the EB-L-3.2K household energy storage system? 2. What risks can safety glasses prevent when setting up the EB-L-3.2K energy storage system? 3. Where can I find the recommended personal protective equipmentguidelines for installing the EB-L-3.2K home battery system? | This is a EB-L-3.2K battery. About installation preparation, the product is a household energy storage system. Improper operation may cause personal injury and property damage. Personal protective tools must be used during the installationn. The following are the recommended personal protective toolls: ● Safety gloves: Prevent the risk of electric shock and scratchesduring the installation. ● Safety glasses: Prevent eye damage from splashing foreign objectsduring the installation. ● Safety Shoes: Prevent the risk of eletric shock. Ensure safety iin case the module is accidentally dropped during the installation. Below is the link of personal protective equipment: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623154621917.png
1. What tools are required for installing the EB-L-3.2K household energy storage system? 2. Where can I find the list of necessary tools for the EB-L-3.2K installation process? 3. Are there any specialized tools needed for assembling the EB-L-3.2K energy storage system? | This is a EB-L-3.2K battery. Tools needed in the process of installing equipment, more effective to improve installation efficiency. Below is the link of installation tools: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623154935527.png
1. What should I check first when unboxing the EB-L-3.2K battery? 2. What steps should I take if I find visible damage on the EB-L-3.2K battery after delivery? 3. How should I properly unpack the EB-L-3.2K energy storage system? 4. Where can I find the packing list to verify accessories for the EB-L-3.2K? 5. What should I do if any items are missing from the EB-L-3.2K battery package? | This is a EB-L-3.2K battery. You should open box to check: ● Make sure the battery is intact during shipping. If there is any vissible damage such as cracks, please contact your dealer immediately. ● Tear off the packaging tapes to unpack the battery. Ensure thaat the battery packaging and all related items are in good condition. ● Please check the packing list carefully by referring to Secction 4.2.4 Packing accessories. If there's any item missing, please contact your dealer directly.
1. Give me a table of detailed product accessories of the EB-L-3.2K battery package. 2. Is there a a list of product accessories of the EB-L-3.2K battery package? | This is a EB-L-3.2K battery. About product accessories, the quantity and function description of each part are listed in below: Label A: The battery is one in quantity and is the core component of the system. Label B: There is one logger which is for system status monitoring. Label C: There is one power cable 1 (quick - plug terminals at both ends/black) and it connects the negative pole between the battery modules. Label D: There is one power cable 2 (quick - plug terminals at both ends/red) and it connects the positive pole between the battery modules. Label E: There is one power cable 3 (quick - plug terminal + SC25 - 6/black) and it connects the negative pole between the battery and the inverter. Label F: There is one power cable 4 (quick - plug terminal + SC25 - 6/red) and it connects the positive pole between the battery and the inverter. Label G: There is one RS485 communication line and it connects the communication interface between battery modules. Label H: There is one CAN communication line and it connects the communication interface between battery and inverter. Label I: There is one metal bracket and its function is to fix the battery. Label J: There are six expansion tubes/screws (diameter 6mm, depth 50mm) and they are for fixed brackets. Label K: There is one ground screw/M4 - 6 and it is connected to the ground terminal. Label L: There are two terminals/SC25 - 6 and they are spare terminals. Label M: There is one terminal/OT4 - 4 and it is connected to the ground wire. Label N: There is one quick installation guide and it is for product installation. The following link provieds detailed information: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623155636564.png
1. What are the steps of installing the EB-L-3.2K battery package? 2. Give me the steps of nstalling the EB-L-3.2K battery package? | This is a EB-L-3.2K battery. About installation, make sure the ground is level and strong enough to bear the weight of products Before you start connecting cables, make sure that the inverter and battery are entirely switched off! Make sure there is no water source above or near the battery, including downspouts, sprinklers, or faucets. Step 1: Drill positioning holes on the wall Use the bracket as a template to mark the position of the 6 heble, then drill 10mm wide holes and make sure the hole depth is more than 50mm. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623155943373.png Step 2: Fix the wall mount bracket Fit the expansion tubes into the holes, pull them tight, and thhen use the expansion screws (packaged with expansion tube for use) to install and secure the wall mount braecket to the wall. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623160030378.png Step 3: Fix the battery There is a hook design on the back of the battery box, align andfix it to the positioning groove of the wall bracket for firm support. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250623160118498.png
1. What should I do before connecting cables for the EB-L-3.2K? 2. For the electrical connection of the EB-L-3.2K, which cable is used to connect the positive pole between the battery modules? 3. How can I ensure the correct connection of positive and negative terminals for the EB-L-3.2K battery during electrical connection? 4. What is the purpose of measuring cable continuity and short circuits before connecting cables for the EB-L-3.2K? 5. Which cable is used to connect the communication interface between the battery and the inverter for the EB-L-3.2K? | This is a EB-L-3.2K battery. About electrical connections, before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling.
1. What types of communication lines and cables are there in the system general wiring diagram of the EB-L-3.2K battery? 2. Which communication line is used for CAN communication in the EB-L-3.2K system general wiring diagram? 3. How many power cables are there in the system general wiring diagram for the EB-L-3.2K battery? 4. What is the purpose of the ground wires in the EB-L-3.2K system general wiring diagram? 5. Where can I get more detailed information about the system general wiring diagram of the EB-L-3.2K battery? | This is a EB-L-3.2K battery. Below is a system general wiring diagram.There are CAN communication lines, RS485 communication lines, power cables (Power cable 1, Power cable 2, Power cable 3, Power cable 4) and ground wires. The following link provides detailed infomation: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624090930898.png
1. Give me a diagram of cable types of EB-L-3.2K battery. 2. What does each cable's function, size and source of EB-L-3.2K battery? | This is a EB-L-3.2K battery. Below is the description of cable types: 1. No.1: Ground wire. Ground the battery with a ground wire. Size: 4mm². Source: Prepared by the customer. 2. No.2: Power cable 1. Connect the negative pole between the battery modules. Size: Black. Source: Delivered with the product. 3. No.3: Power cable 2. Connect the positive pole between the battery modules. Size: Red. Source: Delivered with the product. 4. No.4: Power cable 3. Connect the negative pole between the battery and the inverter. Size: Black. Source: Delivered with the product. 5. No.5: Power cable 4. Connect the positive pole between the battery and the inverter. Size: Red. Source: Delivered with the product. 6. No.6: RS485 communication line. Connect the communication interface between battery modules. Size: Black. Source: Delivered with the product. 7. No.7: CAN communication line. Connect the communication interface between battery and inverter. Size: Black. Source: Delivered with the product. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624091747618.png
1. What's the step of battery ground connection of EB-L-3.2K battery? 2. Give me the step of battery ground connection of EB-L-3.2K battery? | This is a EB-L-3.2K battery. Below are the steps of battery ground connection: 1) Crimp the ground terminal Customer needs to prepare the area of the grounding cable shaall be at least 4mm², use a ground screw and terminal to connect the ground cable. The bolt locking torqueis 2NM. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624092308943.png 2) Ground the battery with a ground wire through the ground screw arnd terminal. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624092321548.png
1. How do I connect cable 1 to cable 2 of EB-L-3.2K batterl? 2. What is the correct wiring method for the EB-L-3.2K baytery system? 3. Which terminals (P+ and P-) should be connected when linking EB-L-3.2K batteries? 4. Is there a diagram available for the power connections of the EB-L-3.2K battery? 5. What cables should be used to interconnect the EB-L-3.2K battery units? | This is a EB-L-3.2K battery. Below is the guide of power connections between batteries: Use power cable 1 to connect the negative pole (P- terminal) of battery A to the negative pole (P-terminal) of battery B, and use power cable 2 to connect the positive pole (P+terminal) of battery A to the positive pole (P+terminal) of battery B. For more than two battery connections, connect the negativee poles (P- terminal) between the batteries and connect the positive poles (P+ terminal) between the batteriees. 1) Connect the negative poles between batteries. 2) Connect the positive poles betweebatteries https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624092820911.png
1. How do I connect cable 1 to cable 2 of EB-L-3.2K battery? 2. Which terminals (P+ and P-) on the EB-L-3.2K battery should be connected to the inverter’s BAT+ and BAT- terminals? 3. What safety precautions should I follow before connecting the EB-L-3.2K battery to the inverter? 4. Can I mix the EB-L-3.2K battery with other brands or different specifications when connecting to the inverter? 5. Is there a wiring diagram available for connecting the EB-L-3.2K battery to an inverter? | This is a EB-L-3.2K battery. Below is the guild of connect the primary battery with the inverter through power cord: After the battery is connected according to Step 1-2, connect the negative pole (P- terminal) of the battery A and the BAT - terminal of the inverter with the power cable 3; connect the positive pole (P+ terminal) of the battery A and the BAT + terminal of the inverter with the power cable 4 Note : Before connecting the inverter electrically, the inverter and baatteries need to be powered off. It is forbidden to mix batteries of different brands, specifications and batches, otherwise it will cause system failure. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624093911770.png
1. How to connect the CAN communication cable of EB-L-3.2K battery? | This is a EB-L-3.2K battery. Below is the guide of connecting the CAN communication cable: Use the CAN communication cable to connect the inverter withthe primary through CAN protocol. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624100158897.png
1. How do I connect the RS485 communication cable between multiple EB-L-3.2K batteries? 2. What are the correct RJ45 pin definitions for the CAN port when connecting the EB-L-3.2K battery to the inverter? 3. Which communication port (CAN or RS485) should be used between the EB-L-3.2K battery and the inverter? 4. What are the RJ45 pin assignments for the RS485 port when linking secondary EB-L-3.2K batteries to the primary unit? 5. Is there a wiring diagram available for the communication connections of the EB-L-3.2K battery system? | This is a EB-L-3.2K battery. Below is the guide of connecting the RS485 communication cable: Use the RS485 communication cable to connect the battery insequence through the RS485 port. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624100341539.png The following link is the sample of communication parallel: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624100455875.png Note: 1) The connection between the inverter and the battery must bbe connected to the CAN communication port of the battery, otherwise communication cannot be perforrmed; the connection between the batteries must be connected to the RS485 port. 2) The communication port pins connecting the primary to the inveerter are defined as follows: In CAN port, RJ45 Pin 4: CANH, RJ45 Pin 5: CANL, RJ45 Pin 6: GND, RJ45 Pin 1/2/3/4/7/8: NC https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624100603405.png 3) The communication port pins connecting the subs to the primary are defined as follows: In RS485 port, RJ45 Pin 1/8: RS485_B, RJ45 Pin 2/7: RS485_A, RJ45 Pin 3/6: GND, RJ45 Pin 4/5: NC https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624100625144.png
1. What is the default DIP setting for the primary EB-L-3.2K battery? 2. How should the DIP switches be configured for a subordinate EB-L-3.2K battery? 3. What do the DIP switch bits (#1 to #6) signify for the EB-L-3.2K battery? 4. What is the address allocation principle when using multiple EB-L-3.2K batteries? 5. How is the primary vs. subordinate EB-L-3.2K battery determined in an inverter-connected system? | This is a EB-L-3.2K battery. About DIP settings, the battery directly connected to the inverter is the primary anad the rest are subordinates. The address allocation principle is binary. The battery addresssetting in the same system cannot be repeated. Definition of DIP code: #1-#4 are address bits ,#5 is communication protocol bit and #6 is primary bit. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624101759204.png Primary DIP setting: DIP address is (1:ON, 2-4:OFF), the batttery factory default settings are the master mode and don't need to be changed. Subordinate DIP setting: Dip address is #1-#4 , #5&#6 need to be dipped OFF.
1. Is there a reference diagram available for the DIP address settings of the EB-L-3.2K battery system? 2. What are the specific DIP switches to be turned ON and OFF for different address configurations of the SUB EB-L-3.2K battery? | This is a EB-L-3.2K battery. The DIP Address of primary and subordinate units are set accordirig to the table below: Address 1: The dip switch for the Primary EnValt (default) and Luxpower has DIP ON as 1 and 6, and DIP OFF as 2, 3, 4, 5. Address 2: The dip switch for the SUB has DIP ON as 2 , and DIP OFF as 1, 3, 4, 5, 6. Address 3: The dip switch for the SUB has DIP ON as 1 and 2 , and DIP OFF as 3, 4, 5, 6. Address 4: The dip switch for the SUB has DIP ON as 1, 2, 4, 5, 6 , and DIP OFF as 3. Address 5: The dip switch for the SUB has DIP ON as 1, 3 , and DIP OFF as 2, 4, 5, 6. Address 6: The dip switch for the SUB has DIP ON as 2, 3 , and DIP OFF as 1, 4, 5, 6. Address 7: The dip switch for the SUB has DIP ON as 1, 2, 3 , and DIP OFF as 4, 5, 6. Address 8: The dip switch for the SUB has DIP ON as 4 , and DIP OFF as 1, 2, 3, 5, 6. Address 9: The dip switch for the SUB has DIP ON as 1, 4 , and DIP OFF as 2, 3, 5, 6. Address 10: The dip switch for the SUB has DIP ON as 2, 4 , and DIP OFF as 1, 3, 5, 6. Address 11: The dip switch for the SUB has DIP ON as 1, 2, 4 , and DIP OFF as 3, 5, 6. Address 12: The dip switch for the SUB has DIP ON as 3, 4 , and DIP OFF as 1, 2, 5, 6. Address 13: The dip switch for the SUB has DIP ON as 1, 3, 4 , and DIP OFF as 2, 5, 6. Address 14: The dip switch for the SUB has DIP ON as 2, 3, 4 , and DIP OFF as 1, 5, 6. Address 15: The dip switch for the SUB has DIP ON as 1, 2, 3, 4 , and DIP OFF as 5, 6. Address 16: The dip switch for the SUB has no DIP ON and DIP OFF as 1, 2, 3, 4, 5, 6. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624102920375.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624102937242.png
1. What is the correct power-on sequence for the EB-L-3.2K battery system? 2. How do I check if the EB-L-3.2K battery indicators are normal before turning on the inverter? 3. What should I do if the 'ALM' light on the EB-L-3.2K battery panel is not off during startup? 4. When powering on the EB-L-3.2K, should the battery or the inverter be activated first? 5. After starting the EB-L-3.2K battery, what is the next step before powering on the inverter? | This is a EB-L-3.2K battery. About equipment power on, after confirming that the cables are connected in the correct ordler and the connections are tight, the system is powered on and activated the system in the following order: 1) Press the battery power switch in turn (first the primary, then the sub) to start the battery. 2) Observe whether the status of the indicator light on the battery jpanel is normal ('RUN' green light flash, ALM' light off). Indicator light is normal can continue in order too power on. If the indicator light is faulty, you need to remove the fault and then power on. 3) Close the circuit breaker between the battery and the inverter 4) The power-up process of the inverter is carried out accordingto the manual process of the inverter.
1. What is the correct shutdown procedure for the EB-L-3.2K battery system? 2. Should I turn off the battery or disconnect the circuit breaker first when powering down the EB-L-3.2K? 3. How do I know if the EB-L-3.2K battery is fully powered off? 4. What should I do if the EB-L-3.2K battery will not be used for a long time? 5. Where can I find maintenance instructions for the EB-L-3.2K battery after prolonged storage? | This is a EB-L-3.2K battery. About equipment power down, after confirming that the load is off and the battery has stoppedcharging and discharging, power down in the following order: 1) Disconnect the circuit breaker on the battery and the circuit brreaker between the battery and the inverter. 2) Turn off the power switch on the battery. 3) Indicator light goes out. If the battery is not working after a long period of time, it is necessary to maintain and recharge the battery in time according to subsections 6.2 and 6.3 of this manual.
1. How do I register and log in to set up the logger for the EB-L-3.2K battery system? 2. What are the steps to create a new station or add devices to an existing station in the EB-L-3.2K monitoring app? 3. How do I connect the EB-L-3.2K logger to a Wi-Fi network during setup? 4. What is the process for binding the EB-L-3.2K logger to a station via Bluetooth? 5. Where can I find the serial number (SN) to confirm successful binding of the EB-L-3.2K logger? | This is a EB-L-3.2K battery. Below are the steps of logger installation: Step 1: Registering and login Tap"Sign up", after filling in the information, click on "Confirm" to log in If you have already registered, you can tap"Sign in" in directly as sheown in Fig. 19. Step 2: Create station Tap" Create station" on the page, as shown in Fig. 20. You will need to fill in information for the new station, as shown in Fig. 21. If you have a station, but need to add new devices to your station. Please tap the "+" button to add devices to your station, as shown in Fig.22. Step 3: Network Connection Select the WiFi network you want to connect to, enter your WiFipassword and tap"Confirm", as shown in Fig.23. Step 4: Bluetooth search Turn on your phone's Bluetooth, then select the devices you want to bind. Tap "Bind with station" to bind the devices to your station, as shown in Fig. 24. The SN on this ppage is the same as the SN on the logger. After the devices are connected to the networkand bound successfully, you will see the page shown in Fig. 25. Step 5: Bluetooth search Please tap the "Go back". Now you can use the APP to view yyour device datal. Figure 19 - 21: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624104146552.png Figure 22 - 24: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624104220269.png Figure 25 - 26: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624104244148.png Please refer to the attached Monitor Usage Guide for the installation and registration of the logger. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624104325984.png
1. What do the first four indicator lights on the EB-L-3.2K battery represent? 2. When does the 'ALM' (Red) light turn on in the EB-L-3.2K battery system? 3. What does the 'RUN' (Green) light indicate on the EB-L-3.2K battery? 4. How can I check the SOC (State of Charge) of the EB-L-3.2K battery using the indicator lights? 5. What happens to the indicator lights when the EB-L-3.2K battery is shut down? | This is a EB-L-3.2K battery. About definition of indicator lights, the indicator light consists of 6 lights, the first 4 lights indicate theSOC of the battery, which are 25%, 50%, 75% and 100% respectively. The fifth 'ALM' light (Red light) is a fauIt indicator, which will light up when the system has a fault. The sixth 'RUN' light is the normal operation light, and the green light will light up when the system is operating normally. When the system shuts downall lights go out.
1. What is the indication of the capacity indicator lights in the "Charge" mode when the state of the EB-L-3.2K battery is 0 - 25% / 25 - 50% / 50 - 75% / 75 - 100%? 2. In the "Discharge" mode, how do the capacity indicator lights of the EB-L-3.2K battery show when its state is 0 - 25% / 25 - 50% / 50 - 75% / 75 - 100%? 3. When in the "Charge" mode, what is the situation of the capacity indicator lights of the EB-L-3.2K battery for the state of 0 - 25% / 25 - 50% / 50 - 75% / 75 - 100%? 4. In the context of the EB-L-3.2K battery, how do the capacity indicator lights behave during the "Discharge" mode for the state of 0 - 25% / 25 - 50% / 50 - 75% / 75 - 100%? 5. For the EB-L-3.2K battery, what is the state corresponding to the situation where in the "Charge" mode, "SOC4", "SOC3", and "SOC2" are on (ON), and "SOC1" flashes (FLASH 2)? | This is a EB-L-3.2K battery. About capacity indicator, the definitions of the indicator lights during the charging arnd discharging process of the battery are shown in the following table. State: 0 - 25% Capacity Indicator: In the "Charge" mode, "SOC4" flashes (FLASH 2), and "SOC3", "SOC2", and "SOC1" are off (OFF). In the "Discharge" mode, "SOC4" is on (ON), and "SOC3", "SOC2", and "SOC1" are off (OFF). Running Lights: In "Charge" mode, the running light is on (ON). In "Discharge" mode, the running light flashes 3 times (FLASH 3). State: 25 - 50% Capacity Indicator: In the "Charge" mode, "SOC4" is on (ON), "SOC3" flashes (FLASH 2), and "SOC2" and "SOC1" are off (OFF). In the "Discharge" mode, "SOC4" and "SOC3" are on (ON), and "SOC2" and "SOC1" are off (OFF). Running Lights: In "Charge" mode, the running light is on (ON). In "Discharge" mode, the running light flashes 3 times (FLASH 3). State: 50 - 75% Capacity Indicator: In the "Charge" mode, "SOC4", "SOC3" are on (ON), "SOC2" flashes (FLASH 2), and "SOC1" is off (OFF). In the "Discharge" mode, "SOC4", "SOC3", and "SOC2" are on (ON), and "SOC1" is off (OFF). Running Lights: In "Charge" mode, the running light is on (ON). In "Discharge" mode, the running light flashes 3 times (FLASH 3). State: 75 - 100% Capacity Indicator: In the "Charge" mode, "SOC4", "SOC3", and "SOC2" are on (ON), and "SOC1" flashes (FLASH 2). In the "Discharge" mode, "SOC4", "SOC3", "SOC2", and "SOC1" are on (ON). Running Lights: In "Charge" mode, the running light is on (ON). In "Discharge" mode, the running light flashes 3 times (FLASH 3). The following link provides detailed information: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624105607835.png
1. Give me a table of definition of the status indicator of the EB-L-3.2K battery. 2. What does each state's abnormal event, LED, ALM and RUN of the EB-L-3.2K battery? | This is a EB-L-3.2K battery. About status indicator, the table below provides detailed information: 1. For the "Shutdown" state with a "Shutdown" abnormal event, the capacity indicators (LED) are ALL OFF, the "ALM" light is "OFF", and the "RUN" light is "FLASH 1". 2. For the "Standby" state with a "Normal" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "OFF", and the "RUN" light is "FLASH 1". 3. For the "Standby" state with an "Alert" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "FLASH 2", and the "RUN" light is "FLASH 1". 4. For the "Charge" state with a "Normal" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "OFF", and the "RUN" light is "ON". 5. For the "Charge" state with an "Alert" abnormal event, the highest indicator LED flashes 2, the "ALM" light is "FLASH 2", and the "RUN" light is "ON". 6. For the "Charge" state with an "Overvoltage protection/Full charge protection" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "OFF", and the "RUN" light is "ON". 7. For the "Charge" state with an "Overcurrent protection (limited current charging)" abnormal event, according to the battery indicator (flashing twice when there is charging current), the "ALM" light is "OFF", and the "RUN" light is "ON". 8. For the "Charge" state with a "Temperature protection" abnormal event, the capacity indicators (LED) are ALL OFF, the "ALM" light is "ON", and the "RUN" light is "OFF". 9. For the "Discharge" state with a "Normal" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "OFF", and the "RUN" light is "FLASH 3". 10. For the "Discharge" state with an "Alert" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "FLASH 2", and the "RUN" light is "FLASH 3". 11. For the "Discharge" state with an "Undervoltage protection" abnormal event, the capacity indicators (LED) follow according to the battery indicator, the "ALM" light is "FLASH 2", and the "RUN" light is "OFF". 12. For the "Discharge" state with an "Overcurrent, short circuit protection" abnormal event, the capacity indicators (LED) are ALL OFF, the "ALM" light is "ON", and the "RUN" light is "OFF". 13. For the "Discharge" state with a "Temperature protection" abnormal event, the capacity indicators (LED) are ALL OFF, the "ALM" light is "ON", and the "RUN" light is "OFF". 14. For the "Fault" state with "NTC fault, MOS fault, reverse connection, differential pressure protection, ultra - low voltage protection" abnormal events, the capacity indicators (LED) are ALL OFF, the "ALM" light is "ON", and the "RUN" light is "OFF". 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624110249059.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624111025582.png
1. How long is the "ON" time when the EB-L-3.2K battery's light flashes once/twice/three times? 2. Based on the given data for the EB-L-3.2K battery, what is the "OFF" time when the light flashes once/twice/three times? 3. Give a table of ON and OFF time of each flashing method of the EB-L-3.2K battery. | This is a EB-L-3.2K battery. About flashing description, the table below provides detailed information: 1. For flashing once, it is 0.25s when on and 3.75s when off. 2. For flashing twice, it is 0.5s when on and 0.5s when off. 3. For flashing three times, it is 0.5s when on and 1.5s when off. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-3.2K/20250624111443966.png
1. What are EB-L-3.2K battery environment requirements? | This is EB-L-3.2K battery. Here's some battery storage information. The battery is required to be stored in a temperature range from 0°C to 40°C. Routine maintenance is required for batteries that have been stored for a long time. Depending on the storage time of the battery and the storage environment, Please charge the battery to the corresponding SOC at 0.2C as required by the table below in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100014207.png ● After a long-time storage, the battery should be inspected and tested by professionals before use. ● During the storage period, record temperature, humidity and storage environment in accordance with storage requirements in this manual. ● Long-term storage of batteries is not recommended, which will cause capacity loss. Generally, after 12 months of storage at the recommended storage temperature, an irreversible capacity loss of lithium batteries is 3%~10%. ● The batteries should be stored in accordance with the labels on the packaging box and should not be inverted or placed sideways. ● The battery boxes should be stacked according to the stacking requirements on the outer packaging. ● When handling the battery, take care not to damage the battery. ● Storage Environment Requirements: Ambient temperature: short-term storage (less than 1 month)0°C~40°C, long-term storage (more than 1 month) 5°C~35°C. Recommended storage temperature: 20°C~30°C. Relative humidity: 5%RH~60%RH. Store products in a dry, clean and ventilated place. Keep them away from dust, direct sunlight, rain, vapor or groundwater. Avoid contact with corrosive organic solvents, gases and other substances.
1. What are EB-L-3.2K battery charging requirements after over-discharge? | This is EB-L-3.2K battery. Here're some charging requirements after over-discharge. The battery stops discharging there is still static power consumpttion of the internal battery module and its own self-discharge loss, if there is no charge for a long time to replenish, it may lead to battery damage due to over-discharge. When the battery SOC is low, it needs to be replenished according to the maximum interval in the table in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100543031.png We do not provide warranty service for permanent battery failure due to overdue recharging by the customer.
1. Can you give me some long-term idle maintenance requirements for EB-L-3.2K battery? | This is EB-L-3.2K battery. Here are some long-term idle maintenance requirements. If a long period of inactivity (≥30 days) is planned, the following two requirements should be observed to protect the battery: 1) Ensure that the battery's SOC system is above 30% and that the battery circuit breaker and power switch remain off. 2) If it is stored for more than 30 days, due to different temperature and different storage time, it has different effects on self-discharge. Therefore, before the battery batteries go online, it is necessary to check the voltage completely to confirm the necessity of maintainirg the state of charge, our company can assist the customer to make a judgment. 3) If the interval between two charges of the battery exceeds 2 months, the standard charging mode should be adopted for 2~3 times before the battery performance can reeach the best state. 4) If it is stored for more than 3 months, it shall be tested and maintained every 3 months. If it is not tested or maintained for more than 9 months, EnValt will not be resporasible for quality protection for capacity loss or other defects caused by batteries. Note: We do not provide appropriate warranty service forpermanent battery failure due to improper storage by the customer.
1. Can you give me some EB-L-3.2K battery maintenance safety requirements? | This is EB-L-3.2K battery. Here are some battery maintenance safety requirements. When the equipment is running, a high voltage may cause electric shocks and result in death, serious injury or property damage. Before performing maintenance, turn off the equipment and strictly follow the safety precautions listed in this manual and other related documents. ● Ensure that you are familiar with the contents of this manual and have appropriate tools and test equipment to perform maintenance. ● Before performing maintenance, turn off the equipment according to the instructions and wait for a certain period of time to ensure that the equipment is power-off. ● During maintenance, prevent unnecessary personnel from getting close to the maintenance site. ● Temporary warning signs or fences must be erected to isolate the site. ● If the equipment fails, please contact your dealer in time to deal with it. ● The equipment can only be power-on again after the fault has been dealt with. Otherwise, the equipment may have some problems or become damaged. ● Do not dissemble the product without authorization. There is a danger of electric shocks and the corresponding failure is not covered by the warranty. ● Maintenance personnel should have received the professional training and use protective tools to conduct maintenance. ● When it is necessary to move or rewire, the input power must be cut off. Wait for 5 minutes to ensure that the internal energy of the machine has been discharged. The maintenance should be started after confirming with a multimeter that there is no dangerous voltage and no parts need to be repaired inside the machine. ● Maintenance of batteries should be performed or supervised by someone who is familiar with batteries and required precautions. ● Please use the same type of cell when replacing cells. ● After maintenance, immediately check that no tools or other parts have been left inside the equipment. ● If the equipment has not been used for a long time, you need to store and charge the battery according to this manual. All operators of the energy storage system shall comply with the user manual. Any equipment damage caused by neglecting or misreading the user manual, will void the product warranty.