## Sheet1
问题 | 答案
1. What hazards can improper operation cause in the EB-L-5.12K battery? 2. What precautions should be taken when using EB-L-5.12K battery? 3. What is the Safety Requirement in the EB-L-5.12K battery? 4. What is the General Requirement in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the General Requirements. The equipment has a high voltage. Irregular operation may generate electricshock or fire which may cause death, severe personal injuries or serious property damages. Please standardize the operation： (1) It is strictly prohibited to install or operate outdoor equipments and cables (including handling equipment, operating equipment and cables, plugging and unplugging signal interfaces connected to the outdoors, working at heights, outdoor installation, etc.) in severe weather such as thunderstorm, snowy weather, strong breeze. (2) Please observe the operation sequence and safety precautions in this manual and other related manuals. (3) Follow the warning signs, cautions and precautions on the equipment. (4) Follow the manual to use correct tools, and master the correct use of tools. (5) Do not install and connect cables, maintain, or replace equipments with power on. (6) Do not wash the equipment. (7) Do not open the panel of the equipment. (8) Measure the voltage before touching conductor surface or terminal to verify that there is no risk of electric shock. (9) Repair the scratches that occur during equipment transportation and installation in time. It is strictly forbidden to expose the scratched parts to the outdoor environment for a long time. (10) It is forbidden to lift and transport the batteries through the battery terminals or bolts. (11) Do not alter the internal structure or installation procedure of the equipment without prior permission of the manufacturer. (12) Leave the building or the equipment area and turn on the fire alarm bell or make an emergency call immediately in the case of a fire. Do not enter the building on fire in any case.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the Personnel Requirement in the EB-L-5.12K battery? 4. What does "Professionals" mean? 5. What does "Trained personnel" mean? 6. What does "Operators" mean? | This is a EB-L-5.12K battery. Below are the Personnel Requirements that require user attention: (1) Personnel installing or maintaining EnValt equipment must be trained, understand all necessary safety precautions, and be able to correctly perform all operations. Personnel who will operate the equipment, including operators, trained personnel and professionals should possess local national required qualifications in special operations such as high-voltage operations and operations of special equipment. (2) Only qualified professionals or trained personnel are allowed to install, operate and maintain the equipment. (3) Only qualified professionals are allowed to remove security facilities and overhaul equipment. (4) Only professionals or authorized personnel are allowed to replace the equipment or components (including software). Here are explanations of the key terms from the above content: (1) Professionals: personnel who are trained or experienced in equipment operations and are clear of the sources and degree of various potential hazards in equipment installation, operation and maintenance. (2) Trained personnel: personnel who are technically trained, have required experience, are aware of possible hazards on themselves in certain operations and are able to take protective measures to minimize the hazards on themselves and other people. (3) Operators: operation personnel who may come into contact with the equipment, except trained personnel and professionals.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the Installation Environment Requirement in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the Installation Environment Requirements. These serve as a warning to users: (1) The installation and operating environment must comply with international, national and local standards for lithium batteries and with local laws and regulations. (2) Install in a location out of the reach of children. (3) Garage installation needs to be far away from the direction of vehicle travel, it is recommended to install the energy storage on the wall above the body bumper to avoid an accidental collision. (4) When installing the battery in a basement, keep good ventilation. Do not place flammable or explosive materials around the battery. It is recommended that the battery be mounted on the wall to avoid contacting with water. (5) Install the battery in a dry and well-ventilated environment. Secure the battery on a solid and flat surface. (6) Install the battery in a sheltered place or install an awning over it to avoid direct sunlight or rain. (7) Install the battery in a clean environment that is free from sources of strong infrared radiation, organic solvents, and corrosive gases. (8) Precautions should be taken for installation in areas with frequent natural disasters such as floods, mudslides, earthquakes and typhoons. (9) Keep the battery away from fire sources. Do not place any flammable or explosive materials around the battery. (10) Keep the battery away from water sources such as taps, sewer pipes, and sprinklers to prevent water seepage. (11) Do not install the battery in a position where it is easy to touch as the temperature of the chassis and heat sink is high when the battery is running. (12) To prevent fire due to high temperature, ensure that the vents and the cooling system are not blocked when the battery is running. (13) Do not expose the battery to flammable, explosive gas or smoke. Do not perform any operation on the battery in such an environment. (14) Do not install the battery on a moving object, such as ship, train or car. (15) Do not install the system outdoors in a salt-affected area because the system may be corroded. A salt- affected area is an area within 500m from the coast or affected by sea breeze. The area affected by the sea breeze varies according to meteorological conditions (such as typhoons and seasonal winds) or topographical conditions (such as DAMS and hills).
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the General Requirement of electricity in the EB-L-5.12K battery? 4. What is the Electrical Requirement in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the General Requirements in the Electrical Requirements. These serve as a danger to users. Before connecting cables, ensure that the product is intact. Otherwise, electric shocks or fire may occur. (1) Ensure that all electrical connections comply with local electrical standards. (2) Ensure that the cables you prepared meet local regulations. (3) Use dedicated insulated tools when performing high-voltage operations.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the DC Operation of electricity in the EB-L-5.12K battery? 4. What is the Electrical Requirement in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the DC Operation in the Electrical Requirements. These serve as a danger to users. Do not connect or disconnect power cables with power-on. Transient contact between the core of the power cable and the conductor will generate electric arcs or sparks, which may cause fire or personal injury. (1) Before connecting cables, cut off the power supply if people may contact energized components. (2) Please ensure that the label on the power cable is correct before connecting the power cord. (3) Disconnect all inputs and operate the equipment only after the equipment is powered off
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the Cabling Requirement of electricity in the EB-L-5.12K battery? 4. What is the Electrical Requirement in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the Cabling Requirements in the Electrical Requirements. These serve as a warning to users. When routing cables, ensure that a distance of at least 30mm exists between the cables and heat-generating components or areas. This prevents damage of the insulation layer of the cables. When the temperature is low, violent impact or vibration may damage the plastic cable sheathing. To ensure safety, comply with the following requirements: (1) Cables can be laid or installed only when the temperature is higher than 0℃. Handle cables with caution, especially at a low temperature. (2) If the storage environment temperature of the cables is below 0°C, the cables must be stored at room temperature for more than 24 hours before laying the cables.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the Personal Safety in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Personal Safety. This serves as a warning to users. Wear proper personal protective equipment during operation. If there is a probability of personal injury or equipment damage, stop the operations and take feasible protective measures immediately. (1) Use tools correctly to avoid hurting people or damaging the equipment. (2) The anti-static gloves must be worn when touching the equipment. Do not wear clothes that can easily generate static electricity. (3) Do not touch the shell when the equipment is running, the temperature of the shell is high, which may cause burns. (4) To ensure personal safety and normal use, it should be grounded reliably before use. (5) When the battery is faulty, the temperature may exceed the burn threshold of the touchable surface. Therefore, avoid touching the battery. (6) The electrolyte is harmful to your skin and eyes, so do not disassemble or damage the battery and avoid contact with the electrolyte. (7) Do not place irrelevant objects on the top of the equipment or insert them into any position of the equipment. (8) Do not place flammable objects around the equipment. (9) To prevent explosions and body injuries, do not place batteries in a fire. (10) Do not place the battery module in water or other liquids. (11) Do not short-circuit the battery terminals or it will cause a fire. (12) Do not use water to clean electrical components inside or outside of a cabinet. (13) Do not stand, rely or sit on the equipment. (14) Do not destroy any module of the equipment. (15) Batteries may cause electric shocks and high short-circuit currents. When using the battery, pay attention to the following points: a）Remove all metal objects from yourself, such as watches and rings. b）Use tools with insulated handles. c）Wear rubber gloves and boots. d）Do not put tools or metal parts on the top of the battery. e）Disconnect the charging power supply before connecting or disconnecting the battery terminal. f）Determine if the battery is unexpectedly grounded. Please remove power from the ground if accidental grounding occurs.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. What is the Battery Safety in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Battery Safety. This serves as a danger to users. Do not expose batteries at high temperatures or around heat-generating sources, such as sunlight, fire sources, transformers and heaters. The battery may cause a fire if overheated. (1) To avoid leakage, overheating or fire, do not disassemble, alter or damage batteries, do not insert foreign objects into batteries or place batteries in water or other liquids. (2) The fire hazard of the lithium-ion battery energy storage system is high. Consider the following safety risks before handling batteries: a) Battery electrolytes can be combustible, toxic and volatile. b) Battery thermal runaway can generate flammable gas and harmful gas such as CO and HF. c) The excessive concentration of flammable gas generated from battery thermal runaway may cause combustion and explosion. (3) The batteries must be stored separately inside the packaging. Do not store batteries together with other materials or in the open air. Do not stack batteries too high. (4) Do not use batteries beyond the warranty period. (5) Do not remove the battery packaging before use. Batteries should be charged during storage by professionals as required. Put batteries back into their packaging after charging during storage. (6) Move batteries in the correct direction. Do not place a battery upside down or tilt it. (7) Protect batteries from impact. Empowering Energy Clean And Affordable 7 (8) Do not perform welding or grinding work around batteries to prevent fire caused by electric sparks or arcs. (9) Use batteries within the temperature range specified in this manual. (10) Do not use damaged batteries (such as damages caused when a battery is dropped, bumped or dented on the enclosure). Damaged batteries may release flammable gases. Do not store damaged batteries near undamaged products. (11) Do not place damaged batteries in close proximity to flammable materials. (12) Monitor damaged batteries during storage for signs of smoke, flammable electrolyte leakage, or heat.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. Introduction to the Label Description in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Label Description. The following link are schematic diagrams of the Label Description. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624091657661.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624091702042.png
1. How can the EB-L-5.12K battery be damaged? 2. What measures should be taken if directly exposed to EB-L-5.12K battery electrolyte? 3. What precautions should be taken when using EB-L-5.12K battery? 4. What is the Safety Requirement in the EB-L-5.12K battery? 5. Introduction to the Damaged Battery in the EB-L-5.12K battery. 6. What are the Emergency Measures in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Damaged Battery in the Emergency Measures. This serves as a danger to users. (1) If the battery is damaged or flooded, it may leak the electrolyte and cause a short circuit fire. (2) If the battery is wet or immersed in the water, do not try to touch it. (3) If the battery seems to be damaged, they are not suitable for use and may be dangerous to personals or property. (4) Avoid touching the leaked liquids or gases in the case of battery leakage or abnormal odor, do not approach the battery and contact professionals immediately. Professionals must wear safety goggles, rubber gloves, gas masks, and protective clothing. (5) Electrolyte is corrosive and can cause irritation and chemical burns. In case of direct contact with the battery electrolyte, do as follows: a) Inhalation: Evacuate contaminated areas, get fresh air immediately and seek immediate medical attention. b) Eye contact: Immediately flush your eyes with water for at least 15 minutes, do not rub your eyes and seek medical attention immediately. c) Skin contact: Wash the affected areas immediately with soap and water and seek medical attention immediately. d) Ingestion: Seek immediate medical assistance.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. Introduction to the Battery Drop Emergency Measures in the EB-L-5.12K battery. 4. What are the Emergency Measures in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the Battery Drop Emergency Measures in the Emergency Measures. (1) If a battery is dropped or violently impacted during installation, internal damage may occur. Do not use such batteries. Otherwise, safety risks such as cell leakage and electric shock may arise. (2) If a dropped battery has obvious damage or abnormal odor, smoke or fire occurs, evacuate the personnel immediately, call emergency services, and contact professionals. Professionals can use fire extinguishing facilities to extinguish the fire under safety protection. (3) If a dropped battery has no obvious deformation or damage and no abnormal odor, smoke or fire occurs, contact professionals to transfer the battery to an open and safe place or contact a recycling company for disposal.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. Introduction to the Fire Emergency Measures in the EB-L-5.12K battery. 4. What are the Emergency Measures in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the Fire Emergency Measures in the Emergency Measures. (1) If a fire occurs, power off the system if it is safe to do so. (2) Use carbon dioxide, FM-200 or ABC dry powder extinguishers to extinguish the fire. (3) Ask firefighters to avoid contacting with high-voltage components during extinguishing fires to prevent the risk of electric shock. (4) Overheating may cause batteries to deform and leak corrosive electrolyte or toxic gas. Keep away from the batteries to avoid skin irritation and chemical burns.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. Introduction to the Battery Recovery Process in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Battery Recovery Process that require user attention: (1) Dispose of used batteries in accordance with local laws and regulations. Do not dispose of batteries as household waste. (2) If the batteries leak or are damaged, contact technical support or a battery recycling company for disposal. (3) If the batteries are out of service life, contact a battery recycling company for disposal. (4) Do not expose batteries to high temperatures or direct sunlight. (5) Do not expose batteries to high humidity or corrosive environments.
1. What precautions should be taken when using EB-L-5.12K battery? 2. What is the Safety Requirement in the EB-L-5.12K battery? 3. Introduction to the EU Declaration of Conformity in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the EU Declaration of Conformity that require user attention. The batteries sold on the European market by EnValt comply with the requirements of the following directives： (1) Electromagnetic compatibility Directive 2014/30/EU (EMC) (2) Battery Directive 2006/66/EC and Amending Directive 2013/56/EU (3) Waste Electrical and Electronic Equipment 2012/19/EU
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the System Composition in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the System Composition in the Product Description. The battery system consists of BMS and battery. The battery consists of a high-performance lithium iron phosphate cell that can be charged and discharged to the load. BMS (Battery Management System) is an intelligent electronic system that manages the charge and discharge of batteries and provides system safety protection.
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Model Identification Description in the EB-L-5.12K battery. 3. What does EB-L-5.12K mean? | This is a EB-L-5.12K battery. Below is the Model Identification Description in the Product Description. The following link is a schematic diagram, which shows the Name of the Product. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624100909807.png
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Model Identification Description in the EB-L-5.12K battery. 3. What does EB-L-5.12K mean? | This is a EB-L-5.12K battery. Below is the Model Identification Description in the Product Description. The following link is a corresponding description list, which shows the Definition of the Product Name. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624100913642.png
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Product Dimension And Weight in the EB-L-5.12K battery. 3. Please show me the Picture of the Product in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Product Dimension And Weight in the Product Description. The following link is a schematic diagram, which shows the Picture of the Product. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624101706403.png
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Product Dimension And Weight in the EB-L-5.12K battery. 3. Please show me the details about Dimension And Weight in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Product Dimension And Weight in the Product Description. The following link is a corresponding description list, which shows the details about Dimension And Weight. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624101711498.png
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Interface Description in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Interface Description in the Product Description. The following link is a schematic diagram, which shows the Interface Location Chart. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624102043478.png
1. What is the Product Description in the EB-L-5.12K battery? 2. Introduction to the Product Parameters in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below are the Product Parameters in the Product Description. The following link is a corresponding description list of the Product Parameters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250711091038754.png
1. Introduction to the Personnel Qualification in the EB-L-5.12K battery. 2. What is the Installation in the EB-L-5.12K battery? 3. What skills are required for installers in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Personnel Qualification in the Installation. Product installers should have received safety technical training, obtained the local electrician certifications and the authorized qualifications for product installation. And installers should be familiar with electrical equipment, accumulate relevant experience and have the following capabilities, including but not limited to: (1) Setup, startup, shutdown, grounding, short-circuiting and repair of electrical equipment. (2) Standardized maintenance and use of protective tools for electrical equipment. (3) Providing emergency assistance for the injured. (4) Complying with local laws, regulations, standards and directives.
1. Introduction to the Installation Environment in the EB-L-5.12K battery. 2. What is the Installation in the EB-L-5.12K battery? 3. What conditions are required for installation location in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Installation Environment in the Installation. Please make sure the installation location meets the following conditions： (1) The building is designed to withstand earthquakes. (2) The floor is flat and hard, and the area has minimal dust and dirt. (3) The ambient environment is cool, dry, well-ventilated, and away from the sea, salt water, humid air, heat sources as well as direct sunlight. (4) Temperature and humidity are kept at a constant level. (5) There are no flammable and explosive items, corrosive gases, including ammonia and acid vapors, and contaminants. (6) The installation location must not be exposed to direct sunlight. (7) The installation location must not be exposed to rain or snow. Here are some notes: (1) If the ambient temperature exceeds the operating range, the battery will stop working to protect itself. The optimal temperature range for battery operation is 15°C to 35°C. Frequent exposure to inappropriate temperature may reduce battery performance and life. (2) When the installation environment of the system does not meet the above shading requirements, users canchoose to use the EnValt outdoor box in combination with the system, or build an installation environmentthat meets the conditions on their own. (3) Please install the system and outdoor box according to the operating requirements. Otherwise, EnValt willnot be liable fofor any warranty ty claims resulting frfrom system damage. The following link is a schematic diagram of Installation Environment. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250711091050921.png
1. Introduction to the Installation Angle in the EB-L-5.12K battery. 2. What is the Installation in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Installation Angle in the Installation. The battery can be installed on the wall. When the battery is installed on the wall, install it on a flat wall and keep the battery parallel to the wall. And don’t install the battery at inclined, horizontal, or upside down positions. The following link is a schematic diagram of Installation Angle. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624104525806.png
1. Introduction to the Installation Space in the EB-L-5.12K battery. 2. What is the Installation in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Installation Space in the Installation. Leave enough space to install the battery. The following link is a schematic diagram of Installation Space. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624104530185.png
1. Introduction to the Personal Protective Equipment in the EB-L-5.12K battery. 2. What is the Installation Preparation in the EB-L-5.12K battery? 3. Can you recommend personal protective tools for me in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Personal Protective Equipment in the Installation Preparation. The product is a household energy storage system. Improper operation may cause personal injury and property damage. Personal protective tools must be used during installation. The following are the recommended personal protective tools: (1) Safety gloves: Prevent the risk of electric shock and scratches during installation. (2) Safety glasses: Prevent eye damage from splashing foreign objects during installation. (3) Safety Shoes: Prevent the risk of eletric shock. Ensure safety in case the module is accidentally dropped during installation. The following link is a schematic diagram of Personal Protective Equipment. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624104919899.png
1. Introduction to the Installation Tools in the EB-L-5.12K battery. 2. What is the Installation Preparation in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below are the Installation Tools in the Installation Preparation. Tools needed in the process of installing equipment, more effective to improve installation efficiency. The following link is a schematic diagram of Installation Tools. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624105508904.png
1. Introduction to the Open Box to Check in the EB-L-5.12K battery. 2. What is the Installation Preparation in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Open Box to Check in the Installation Preparation. (1) Make sure the battery is intact during shipping. If there is any visible damage such as cracks, please contact your dealer immediately. (2) Tear off the packaging tapes to unpack the battery, please check that the battery packaging and all related items are in good condition. (3) Please check the packing list carefully by referring to "Product accessories". If there's any item missing, please contact your dealer directly.
1. Introduction to the Product Accessories in the EB-L-5.12K battery. 2. What is the Installation Preparation in the EB-L-5.12K battery? 3. I want to konw the Accessory Description with my EB-L-5.12K. | This is a EB-L-5.12K battery. Below is the Product Accessories in the Installation Preparation. The following link is a corresponding description list of the Accessory Description. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624110039336.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624110043466.png
1. Introduction to the Battery Pack Installation in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Battery Pack Installation. Make sure the ground is level and strong enough to bear the weight of products. Before you start connecting cables, make sure that the inverter and battery are entirely switched off! Make sure there is no water source above or near the battery, including downspouts, sprinklers, or faucets. Here are the steps of the Battery Pack Installation: (1) Locate drill holes in the wall: Use the bracket as a template to make positioning holes in the wall, mark the positions of the 4 holes, and then drill 10mm holes to ensure that the depth of the holes is greater than 50mm. The bracket should be placed at least 550mm above the ground. The following link is a schematic diagram, which shows sample of step 1 for wall installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624111439202.png (2) Fix the wall mount bracket: Fit the expansion tubes into the holes, pull them tight, and then use the expansion screws (packaged with expansion tube for use) to install and secure the wall mount bracket to the wall. The following link is a schematic diagram, which shows sample of step 2 for wall installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624111446119.png (3) Fix the battery module: There is a hook design on the back of the battery box, align and fix it to the positioning groove of the wall bracket for firm support. The distance between the batteries is 300-350mm, and the distance between the battery and the inverter is not less than 400mm. The following link is a schematic diagram, which shows sample of step 3 for wall installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624111448618.png
1. Introduction to the Electrical Connections in the EB-L-5.12K battery. 2. Before connecting the cables of EB-L-5.12K battery, What do I need to pay attention to? 3. Can you show me a System General Wiring Diagram in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is System General Wiring Diagram in the Electrical Connections. Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling. The following link is a schematic diagram of System General Wiring Diagram. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624141351161.png
1. Introduction to the Electrical Connections in the EB-L-5.12K battery. 2. Before connecting the cables of EB-L-5.12K battery, What do I need to pay attention to? 3. Can you show me a description list of Preparing Cables in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is Preparing Cables in the Electrical Connections. Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling. The following link is a corresponding description list of Preparing Cables. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624141418503.png
1. Introduction to the Electrical Connections in the EB-L-5.12K battery. 2. Before connecting the cables of EB-L-5.12K battery, What do I need to pay attention to? 3. What is about the Battery Ground Connection in the EB-L-5.12K battery? 4. Show me a schematic diagram about crimping method in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Battery Ground Connection in the Electrical Connections. Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling. The customer should prepare a ground cable with a cross-sectional area of at least 6mm², then use a ground screw and terminal to connect the ground cable, and ground the battery. The bolt locking torque is 6NM. The following link is a schematic diagram, which shows Sample of crimping method. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624141901438.png The following link is a schematic diagram, which shows Sample of Battery Ground Connection. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624141906990.png
1. Introduction to the Electrical Connections in the EB-L-5.12K battery. 2. Before connecting the cables of EB-L-5.12K battery, What do I need to pay attention to? 3. What is about the Power Connections Between Batteries in the EB-L-5.12K battery? 4. Show me a schematic diagram about Power Connections Between Batteries in the EB-L-5.12K battery. 5. Details about wiring of battery parallel in the EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Power Connections Between Batteries in the Electrical Connections. Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling. Use power cable 1 to connect the negative pole (P- terminal) of battery A to the negative pole (P- terminal) of battery B, and use power cable 2 to connect the positive pole (P+ terminal) of battery A to the positive pole (P+terminal) of battery B. For more than two battery connections, connect the negative poles (P- terminal) between the batteries and connect the positive poles (P+ terminal) between the batteries. The following link is a schematic diagram, which shows Sample of Power Connections Between Batteries. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624151325898.png
1. Introduction to the Electrical Connections in the EB-L-5.12K battery. 2. Before connecting the cables of EB-L-5.12K battery, What do I need to pay attention to? 3. What is about the Connect the Battery to the Inverter Power Supply in the EB-L-5.12K battery? 4. Show me a schematic diagram about Connection for Inverter in the EB-L-5.12K battery. 5. Details about wiring between EB-L-5.12K battery and Inverter. | This is a EB-L-5.12K battery. Below is Connect the Battery to the Inverter Power Supply in the Electrical Connections. Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling. After the battery is connected according to Step 1-2, connect the negative pole (P- terminal) of the battery A and the BAT - terminal of the inverter with the power cable 3; connect the positive pole (P+ terminal) of the battery A and the BAT + terminal of the inverter with the power cable 4. The following link is a schematic diagram, which shows Sample of Connection for Inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250624151331264.png Note: 1) Before the inverter is connected to power cable, the inverter and batteries need to be powered off. 2) It is forbidden to mix batteries of different brands, specifications and batches, otherwise it will cause system failure.
1. Introduction to the Communication Connection in the EB-L-5.12K battery. 2. What is the CAN communication cable used for in the EB-L-5.12K battery? 3. What interface is used for communication between the inverter and EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is Connect the CAN Communication Cable in the Communication Connection. Use the CAN communication cable to connect the inverter to the battery’s CAN port.
1. Introduction to the Communication Connection in the EB-L-5.12K battery. 2. What is the RS485 communication cable used for in the EB-L-5.12K battery? 3. What interface is used for communication between the EB-L-5.12K battery? 4. Show me the wiring of Communication between EB-L-5.12K battery and inverter. 5. Show me the wiring of Communication Parallel with battery in the EB-L-5.12K battery. 6. In the EB-L-5.12K battery, give me details about the definition of CAN Port Pins. 7. In the EB-L-5.12K battery, give me details about the definition of RS485 Port Pins. | This is a EB-L-5.12K battery. Below is Connect the RS485 Communication Cable Between Batteries in the Communication Connection. Use the RS485 communication cable to connect the adjacent batteries in sequence through the RS485 port. The following link is a schematic diagram, which shows Sample of Connection for the Communication Cable. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625091457816.png The following link is a schematic diagram, which shows Sample of Communication Parallel in battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625091453720.png Note: (1) The communication between the inverter and the battery must be connected to the CAN communication port of the battery, otherwise communication cannot be performed; the communication between the batteries must be connected to the RS485 port. The following link is a schematic diagram of Interface icon. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625092314717.png (2) The following link is a corresponding description list(CAN Port Pins), which shows the definition of the communication port pins connecting the primary to the inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625092317869.png (3) The following link is a corresponding description list(RS485 Port Pins), which shows the definition of the communication port pins connecting the subs to the primary. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625092326058.png
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Can you show me the Definition of DIP in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is the Equipment Debugging. Definition of DIP code: #1&#2 are communication protocol bits. The following link is a schematic diagram, which shows the Definition of DIP. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625092926861.png
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Details about Address Setting of EB-L-5.12K battery. 3. How does the system assign the address of each EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is Address Setting in the Equipment Debugging. The battery directly connected to the inverter is the primary and the rest are subordinates. Description of automatic address allocation: After the batteries are activated by pressing the switch in sequence, the system will automatically identify the primary and subordinates and actively assign the address of each device in the system.
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Details about the system power on in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Equipment Power On in the Equipment Debugging. After confirming that the cables are connected in the correct order and the connections are tight, the system is powered on and switched on in the following order: 1) Press the battery power switch in turn (first the primary 01, then the sub 02~16) to start the battery. 2) Observe whether the status of the indicator light on the battery panel is normal ( ‘RUN’ green light flash, ‘ALM’ light off ). Indicator light is normal can continue in order to power on. If the indicator light is faulty, you need to remove the fault and then power on. 3) Close the circuit breaker on the battery and the circuit breaker between the battery and the inverter. 4) The power-up process of the inverter is carried out according to the manual process of the inverter
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Details about the Inverter Protocol Selection in EB-L-5.12K battery. 3. If Inverter brands use the CAN communication protocol, what is the selection of the Primary DIP Address in the EB-L-5.12K battery? 4. If Inverter brands use the RS485 communication protocol, what is the selection of the Primary DIP Address in the EB-L-5.12K battery? 5. Give me the description list of DIP Switch Settings in the EB-L-5.12K battery. 6. what does DIP Switch mean in the EB-L-5.12K battery? | This is a EB-L-5.12K battery. Below is Inverter Protocol Selection in the Equipment Debugging. The battery default factory CAN communication is EnValt protocol and RS485 communication is SRNE protocol. Protocol selection: 1) Check which protocols are supported by the inverter. 2) If the inverter supports the battery factory default protocol, select the corresponding protocol on the inverter directly. 3) If the inverter supports protocols other than the battery factory default protocol, select the same protocol on the battery and the inverter. Battery protocol selection: Select the protocol in the #1&#2 position of the primary DIP Address. (1) If Inverter brands use the CAN communication protocol need to set the Primary DIP Address. The following link is a corresponding description list of DIP Switch Settings for CAN Communication. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625094757307.png (2) If Inverter brands use the RS485 communication protocol need to set the Primary DIP Address. The following link is a corresponding description list of DIP Switch Settings for RS485 Communication. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625094801796.png
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Details about the system power down in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Equipment Power Down in the Equipment Debugging. After confirming that the load is off and the battery has stopped charging and discharging, power down in the following order: 1) Disconnect the circuit breaker on the battery and the circuit breaker between the battery and the inverter. 2) Turn off the power switch on the battery. 3) Indicator light goes out. If the battery is not working after a long period of time, it is necessary to maintain and recharge the battery in time according to user manual.
1. What is the Equipment Debugging in the EB-L-5.12K battery? 2. Details about the Logger Installation in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Logger Installation in the Equipment Debugging. Use an L-shaped hexagonal tool to tighten the two M3*8 screws to secure the logger. The following link is a schematic diagram of Logger Installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625095705480.png After installing the logger, please follow the steps below for registration and connection: Step 1: Registering and login Tap"Sign up", after filling in the information, click on "Confirm" to log in. If you have already registered, you can tap"Sign in" in directly as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100544360.png Step 2: Create station Tap”Create station”on the page, as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100550852.png You will need to fill in information for the new station, as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100557013.png If you have a station, but need to add new devices to your station. Please tap the "+" button to add devices to your station, as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100611826.png Step 3: Network Connection Select the WiFi network you want to connect to, enter your WiFi password and tap"Confirm", as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100622406.png Step 4: Bluetooth search Turn on your phone's Bluetooth, then select the devices you want to bind. Tap "Bind with station" to bind the devices to your station, as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100629043.pngThe SN on this page is the same as the SN on the logger. After the devices are connected to the networkand bound successfully, you will see the page shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100635345.png Step 5: Bluetooth search Please tap the "Go back". Now you can use the APP to view your device datal, as shown in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100640296.png Please refer to the attached Monitor Usage Guide for the installation and registration of the logger. The following link is a schematic diagram of the Logger and Usage Guide. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625100647013.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is the Definition of Indicator Lights. The indicator light consists of 6 lights, the first 4 lights indicate the SOC of the battery, which are 25%, 50%, 75% and 100% respectively. The fifth ‘ALM’ light (Red light) is a fault indicator, which will light up when the system has a fault. The sixth ‘RUN’ light is the normal operation light, and the green light will light up when the system is operating normally. When the system shuts down, all lights go out.
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. Details about Capacity Indicator in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. The following link is a corresponding description list, which shows the definitions of the indicator lights during the charging and discharging process of the battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625104344752.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the capacity indicator is 0～25% in EB-L-5.12K battery, what are the Capacity Indicator Lights? | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. When the capacity indicator is 0～25%, the Capacity indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625105753496.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the capacity indicator is 25～50% in EB-L-5.12K battery, what are the Capacity Indicator Lights? | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. When the capacity indicator is 25～50%, the Capacity indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625105758508.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the capacity indicator is 50～75% in EB-L-5.12K battery, what are the Capacity Indicator Lights? | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. When the capacity indicator is 50～75%, the Capacity indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625105807004.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the capacity indicator is 75～100% in EB-L-5.12K battery, what are the Capacity Indicator Lights? | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. When the capacity indicator is 75～100%, the Capacity indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625105816371.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state is Running lights in EB-L-5.12K battery, what are the Capacity Indicator Lights? | This is a EB-L-5.12K battery. Below is Capacity Indicator in the Definition of Indicator Lights. When the state is Running lights, the Capacity indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625105821123.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. Details about Status Indicator in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. The following link is a corresponding description list, which shows the definitions of the Status indicator lights. 1.https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625104432415.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625104526809.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state of EB-L-5.12K battery is Shutdown, what are the Status Indicator Lights? | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. When the state of battery is Shutdown, the Status indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111033605.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state of EB-L-5.12K battery is Standby, what are the Status Indicator Lights? | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. When the state of battery is Standby, the Status indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111038874.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state of EB-L-5.12K battery is Charge, what are the Status Indicator Lights? | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. When the state of battery is Charge, the Status indicator lights are shown as the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111043060.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state of EB-L-5.12K battery is Discharge, what are the Status Indicator Lights? | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. When the state of battery is Discharge, the Status indicator lights are shown as the following link. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111049958.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111056223.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. When the state of EB-L-5.12K battery is Fault, what are the Status Indicator Lights? | This is a EB-L-5.12K battery. Below is Status Indicator in the Definition of Indicator Lights. When the state of battery is Fault, the Status indicator lights are shown as the following link. 1.https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111100624.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625111105235.png
1. Introduction to the Definition of Indicator Lights in EB-L-5.12K battery. 2. Details about Flash Discription in EB-L-5.12K battery. | This is a EB-L-5.12K battery. Below is Flash Discription in the Definition of Indicator Lights. The following link is a corresponding description list, which shows the definitions of the Flash Discription. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/EB-L-5.12K/20250625104531376.png
1. What're EB-L-5.12K battery environment requirements? | This is EB-L-5.12K battery. Here's some battery storage information. The battery is required to be stored in a temperature range from O°C to +40°C. Routine maintenance is required for batteries that have been stored for a long time. Depending on the storage time of the battery and the storage environment, Please charge the battery to the corresponding SOC at 0.2C as required by the table below in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100014207.png After a long-time storage, the battery should be inspected and tested by professionals before use. During the storage period, record temperature, humidity and storage environment in accordance with storage requirements in this manual. Long-term storage of batteries is not recommended, which will cause capacity loss. Generally, after 12 months of storage at the recommended storage temperature, an irreversible capacity loss of lithium batteries is 3%~10%. The batteries should be stored in accordance with the labels on the packaging box and should not be inverted or placed sideways. The battery boxes should be stacked according to the stacking requirements on the outer packaging. When handling the battery, take care not to damage the battery. Storage Environment Requirements: Ambient temperature: short-term storage (less than 1 month)O°C~~40°C, long-term storage (more than 1 month)5°C~35°C. Recommended storage temperature: 20°C~30°C. Relative humidity: 5%RH~60%RH. Store products in a dry, clean and ventilated place. Keep them away from dust, direct sunlight, rain, vapor or groundwater. Avoid contact with corrosive organic solvents, gases and other substances.
1. What're EB-L-5.12K battery charging requirements after over-discharge? | This is EB-L-5.12K battery. Here're some charging requirements after over-discharge. The battery stops discharging there is still static power consumpttion of the internal battery module and its own self-discharge loss, if there is no charge for a long time to replenish, it may lead to battery damage due to over-discharge. When the battery SOC is low, it needs to be replenished according to the maximum interval in the table in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100543031.png We do not provide warranty service for permanent battery failure due to overdue recharging by the customer.
1. Can u give me some long-term idle maintenance requirements for EB-L-5.12K battery? | This is EB-L-5.12K battery. Here are some long-term idle maintenance requirements. If a long period of inactivity (≥30 days) is planned, the following two requirements should be observed to protect the battery: 1) Ensure that the battery's SOC system is above 30% and that the battery circuit breaker and power switch remain off. 2) If it is stored for more than 30 days, due to different temperature and different storage time, it has different effects on self-discharge. Therefore, before the battery batteries go online, it is necessary to check the voltage completely to confirm the necessity of maintainirg the state of charge, our company can assist the customer to make a judgment. 3) If the interval between two charges of the battery exceeds 2 months, the standard charging mode should be adopted for 2~3 times before the battery performance can reeach the best state. 4) If it is stored for more than 3 months, it shall be tested and maintained every 3 months. If it is not tested or maintained for more than 9 months, EnValt will not be resporasible for quality protection for capacity loss or other defects caused by batteries. Note: We do not provide appropriate warranty service forpermanent battery failure due to improper storage by the customer.
1. Can u give me some EB-L-5.12K battery maintenance safety requirements? | This is EB-L-5.12K battery. Here are some battery maintenance safety requirements. When the equipment is running, a high voltage may cause electric shocks and result in death, serious injury or property damage. Before performing maintenance, turn off the equipment and strictly follow the safety precautions listed in this manual and other related documents. Ensure that you are familiar with the contents of this manual and have appropriate tools and test equipment to perform maintenance. Before performing maintenance, turn off the equipment according to the instructions and wait for a certain period of time to ensure that the equipment is power-off. During maintenance, prevent unnecessary personnel from getting close to the maintenance site. Temporary warning signs or fences must be erected to isolate the site. If the equipment fails, please contact your dealer in time to deal with it. The equipment can only be power-on again after the fault has been dealt with. Otherwise, the equipment may have some problems or become damaged. Do not dissemble the product without authorization. There is a danger of electric shocks and the corresponding failure is not covered by the warranty. Maintenance personnel should have received the professional training and use protective tools to conduct maintenance. When it is necessary to move or rewire, the input power must be cut off. Wait for 5 minutes to ensure that the internal energy of the machine has been discharged. The maintenance should be started after confirming with a multimeter that there is no dangerous voltage and no parts need to be repaired inside the machine. Maintenance of batteries should be performed or supervised by someone who is familiar with batteries and required precautions. Please use the same type of cell when replacing cells. After maintenance, immediately check that no tools or other parts have been left inside the equipment. If the equipment has not been used for a long time, you need to store and charge the battery according to this manual. All operators of the energy storage system shall comply with the user manual. Any equipment damage caused by neglecting or misreading the user manual, will void the product warranty.
1. What is the cell capacity of the EB-L-5.12K battery? 2. What are the rated current and rated voltage of this EB-L-5.12K battery? 3. What is the full charging time of this EB-L-5.12K battery? 4. What is the charge/discharge rate (C-rate) of the EB-L-5.12K battery? 5. What are the nominal current and nominal voltage of this EB-L-5.12K battery? | This is EB-L-5.12K battery. The nominal energy of this battery is 5120Wh, with a nominal voltage of 51.2V and a nominal current of 100A. The cell capacity equals the nominal energy divided by the nominal voltage, which is 100Ah. The full charging time equals the cell capacity divided by the nominal current, i.e., 1C charge/discharge.