## Sheet1
问题 | 答案
1. What safety notes should i know during EM-T1/T3/T5-G1 smart meter installation? | This is EM-T1/T3/T5-G1 smart meter. Here are some safety notes. 1. Before installation, please read this manual carefully and follow the instructions in this manual strictly. 2. Installers need to undergo professional training or obtain electrical related professional qualification certificates. 3. Apart from performing work at the wiring terminal (as instructed in this manual), touching or changing components without authorization may cause injury to people, damage to inverters and annulment of the warranty. 4. All electrical installations must conform to local electrical safety standards. 5. If the meter needs maintenance, please contact the local designated personnel for system installation and maintenance.
1. Under what circumstances, ur company has the right not to bear EM-T1/T3/T5-G1 smart quality assurance? | This is EM-T1/T3/T5-G1 smart meter. Under any of the following circumstances, it has the right not to bear the quality assurance: 1. Damages caused by improper transportation. 2. Damages caused by incorrect storage, installation or use. 3. Damages caused by installation and use of equipment by non-professionals or untrained personnel. 4. Damages caused by failure to comply with the instructions and safety warnings in this document. 5. Damages of running in an environment that does not meet the requirenments stated in this document. 6. Damages caused by operation beyond the parameters specified in applicable technical specifications. 7. Damages caused by unauthorized disassembly, alteration of products modification of software codes. 8. Damages caused by abnormal natural environment (force majeure, such as lightning, earthquake, fire, storm, etc.). 9. Any damages caused by the process of installation and operation which don't follow the local standards and regulations. 10. Products beyond the warranty period.
1. Can u make a basic introduction of EM-T1/T3/T5-G1 smart meter? 2. Can u show me a schematic diagram of EM-T1/T3/T5-G1 smart meter connected with inverter? | This is EM-T1/T3/T5-G1 smart meter. iESS-M1/M5 are smart meters and support different voltage levels and power grid. The iESS-M1/M5 can collect the data in real time, including grid voltage, current, power and energy yield. By cooperating with monitoring system, EM-T1/T3/T5-G1 can realize real-time monitoring of load consumption. The following link is a schematic diagram of EM-T1/T3/T5-G1 smart meter connected with inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627094910221.png Note: More application scenarios of EM-T1/T3/T5-G1 are still under development, please contact us for details.
1. Can u show me a schematic diagram of EM-T1/T3/T5-G1 smart meter apperance? 2. Can u show me a schematic diagram of iESS-M1/M3 smart meter's CT's appearance? | This is EM-T1/T3/T5-G1 smart meter. The following link is a schematic diagram of EM-T1/T3/T5-G1 smart meter appearance. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627095146336.png The following link is a schematic diagram of iESS-M1/M3 CT appearance. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627095521682.png NOTE: If choose the iESS-M5 meter, customers need to purchase their own CTS. The iESS-M5 meter can support up to 5000A/5A CTS. The following link is a table of wiring terminals. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627095731175.png NOTICE: This meter can only be matched with the CT shipped with the meter, and manufacturer will not be responsible for malfunctions if not use the CT shipped with the meter. NOTE: The iESS-M1/M3 will be delivered with matched CT(s) supplied are calibrated and tested to be used with the device in this package. These CT(s) cannot be interchanged within the same device and cannot be used for other devices from other packaging. NOTE: The iESS-M5 is not delivered with CT. Customers are required to purchase qualified standard CT with secondary side output of 5A, CT accuracy of 0.5, and maximum CT conversion ratio of 5000:5.
1. What's the packing list of EM-T1/T3/T5-G1 smart meter? | This is EM-T1/T3/T5-G1 smart meter. The following link is a table of packing list. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627100141160.png
1. What should i notice in EM-T1/T3/T5-G1 smart meter storage? | This is EM-T1/T3/T5-G1 smart meter. Here are storage notes about it. 1. Do not dispose of the original packing case. It is recommended to store the device in the original packing case when the device is decommissioned. 2. The storage temperature and humidity should be in the range of-30°C~+ 60°C, and less than 90%, respectively.
1. Why is reversed CT direction strictly prohibited during EM-T1/T3/T5-G1 smart meter commissioning? 2. How to install EM-T1/T3/T5-G1 smart meter? 3. How to install CT of EM-T1/T3/T5-G1 smart meter? | This is EM-T1/T3/T5-G1 smart meter. iESS-M1 series is IP20 and can be installed indoors only. Here are some installation steps. 1. Smart Meter 1) Pull to release the retaining clip. 2) Mount the meter on the track and push the Retaining clip up(a click sound indicates it is installed well). The following link is a schematic diagram of smart meter installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627100553418.png 2. Current Transformer The following link is a schematic diagram of CT installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627100659115.png NOTE: The installation direction of the CT varies according to the application scenario. Please follow the directions of the CT as shown in 3.1 System Introduction. Incorrect connection or direction will cause incorrect data.
1. Can u show me a schematic diagram of EM-T1/T3/T5-G1 smart meter's screen? 2. When the LAN indicator is slow flashing on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? 3. When the LAN indicator is always on on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? 4. When the LAN indicator is off on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? 5. When the network status is always on on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? 6. When the network status is slow flashing on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? 7. When the network status is off on EM-T1/T3/T5-G1 smart meter's screen, what does it mean? | This is EM-T1/T3/T5-G1 smart meter. The following link is a schematic diagram of its screen which includes indicator area and display area. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627101121775.png There are some indicators on the screen. When the network status is slow flashing, that means iESS-M1 smart meter is connecting to the cloud. When the network status is always on, that means iESS-M1 smart meter is connected to the cloud. When the network status is off, that means no network. When the LAN is slow flashing, that means iESS-M1 smart meter is connecting to the router via LAN. When the LAN is always on, that means iESS-M1 smart meter is connected to the router via LAN. When the LAN is off, that means no network cable is plugged in the iESS-M1 smart meter. When WiFi is slow flashing, that means iESS-M1 smart meter is connecting to router via WiFi. When WiFi is always on, that means iESS-M1 smart meter is connected to router via WiFi. When WiFi is off, that means iESS-M1 smart meter is no network or using LAN port. The following link is a table of indicator on EM-T1/T3/T5-G1 smart meter screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627101904664.png Tips: When the cable is plugged in, WiFi is automatically turned off.
1. What are key instructions on EM-T1/T3/T5-G1 smart meter's screen's functions? | This is EM-T1/T3/T5-G1 smart meter. The following link is a schematic diagram of its screen which includes indicator area and display area. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627101121775.png There are some key instructions on its screen. The following link is a table of these key instructions functions. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627102557473.png
1. Can u show me a schematic diagram of display interface on EM-T1/T3/T5-G1 smart meter's screen? | This is EM-T1/T3/T5-G1 smart meter. The following link is a schematic diagram of its screen which includes indicator area and display area. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627101121775.png The following link is a schematic diagram of its diaplay interface. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627102735750.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627102913835.png
1. Can u show me a schematic diagram of EM-T1/T3/T5-G1 smart meter's settings? | This is EM-T1/T3/T5-G1 smart meter. The following link is a schematic diagram of its settings. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250717155250545.png NOTE: If your CT is 200A/1A then set the ratio to 200:1. If your CT is 800A/5A then set the ratio to 160:1. If your CT is 1500A/5A then the ratio is set to 300:1. And so on, the largest CT supported is 5000A/5A which is 1000:1.
1. How to do EM-T1/T3/T5-G1 smart meter's WiFi configuration? | This is EM-T1/T3/T5-G1 smart meter. There are some steps of its WiFi configuration. Please download the HNAHCU ESS app by scanning the QR code or from the APP Store. Step 1: Select the home WiFi network you want to connect to (not 5G WiFi) and enter your WiFi password. Step 2: Turn on your phone's Bluetooth, then select the devicees you want to bind. Tap "Add" to add the devices to your station. The following link is a schematic diagram of step 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627103301045.png Step 3: After the devices are connected to the network and bound successfully, you will see the page shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627103506488.png
1. Can u tell me some technical parameters of EM-T1/T3/T5-G1 smart meter? | This is EM-T1/T3/T5-G1 smart meter. The following link is a table of its technical parameters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250717155659622.png
1. What information u need to provide me assistance in terms of EM-T1/T3/T5-G1 smart meter? | This is EM-T1/T3/T5-G1 smart meter. Should you have any question about this product, please contact us. We need the following information to provide you the best assistance: Model of the device Serial number of the device Date of the device Fault code/name Brief description of the problem