## Sheet1
问题 | 答案
1. Why must EPortal-G1 installers hold electrical power system certifications? 2. Why is installing EPortal-G1 in wet/damp locations strictly prohibited? 3. Why must cable knockouts be fully sealed after EPortal-G1 installation? 4. Why can’t EPortal-G1 be installed near sources of corrosive gases? 5. Why is direct sunlight exposure unacceptable for EPortal-G1 installations? | This is EPortal-G1. Please follow the equipment installation steps process to ensure the equipment can be successfully installed. The following link is a flow chart of installation steps. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626165913097.png Please ensure that the installer meets the following requiremeents: This system should only be installed by personnel with training and adequate knowledge of electrical power systems. Please ensure that the installation location meets the folllowing conditions: The installation and use environment need to comply with local laws and regulations and relevant international national. Install in a dry, well-ventilated environment and secure the equipmernt on a sturdy, level support surface. Avoid water accumulation in the installation location, and keeep away from water sources such as faucets, sewer pipes, spprinklers, etc. to avoid water infiltration. The environment around the installation location is clean, and there is no large amount of infrared radiation, organic solvents and corrosive gases, etc. Please choose a sheltered installation site, or build a awning to avoiid direct sunlight or rain. Each cable knockouts should be completely sealed in case unexpectted invasions such as insects causing short-circuit.
1. Can u show me a schematic diagram of EPortal-G1 interface? | This is EPortal-G1. The definition of each interface must be clear during the installation process, otherwise the wrong connection will lead to installation failure or even damage to the equipment. The following link is a schematic diagram of EPortal-G1 interface from front, side and bottom views. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626171111883.png
1. What packing items of EPortal-G1 should i check? | This is EPortal-G1. Please refer to the packing items shown in the schematic diagram in the following link https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626171250964.png , please check the packing list carefully, if any items are missing, please contact your dealer directly.
1. What protective equipment products should i prepare during EPortal-G1 installation process? | This is EPortal-G1. Protective equipment products must be worn and maintained during the installation process. The following link is a schematic diagram of protective equipment products during HESS-Gatwway-M1 installation process. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626171613696.png
1. What EPortal-G1 installation tools do i need? | This is EPortal-G1. Installation Tools: tools needed in the process of installing equipment, more effective to improve installation efficiency. The following link is a schematic diagram of EPortal-G1 installation tools. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626171829991.png
1. How to install EPortal-G1? | This is EPortal-G1. Before you start connecting cables, make sure that gateway and the equipment is fully switched off! Make sure the wall is strong enough to bear the weight of the gateway. Step 1: Locate drill holes in the wall Use the bracket as a template to make positioning holes in the wall, mark the positions of the 4 holes, and then drill 10mm holes to ensure that the depth of the holes is greater than 50mm. The bracket should be placed at least 500mm above the ground. The following link is a schematic diagram of step 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626172102802.png Step 2: Fix the wall mount bracket Fix the expansion tubes into the holes, pull them tight, and then use the expansion screws (packaged with expansion tube for use) to install and secure the wall mount bracket to the wall. The following link is a schematic diagram of step 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626172343455.png Step 3: Fix the gateway There is a hook design on the back of the gateway. Align and fix it to the positioning groove of the Wall mount bracket, and secure it with M4*14 screws. Make sure there is enough space around the gateway. The following link is a schematic diagram of step 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626172451101.png
1. Why is using a ground cable below 6mm² strictly prohibited for EPortal-G1? 2. Why must the EPortal-G1 ground bolt torque never exceed 2N·m? 3. Why are unlabeled power cables critical safety violations for EPortal-G1? 4. Why does EPortal-G1 require inverters/loads to share its ground point? | This is EPortal-G1. When it comes to power cable connection, Installation Preparation: 1. Before operation, please make sure all power supplies to the equipment have been disconnected, including but not limited to the grid side and inverter power switches. 2. Using the key to open the equipment door. 3. Loosen the waterproof socket connector under the gateway. Tighten it after the cable installation. Cable Connection: 1. Connect the gateway ground cable The area of the grounding cable shall be prepared at least 6, usinig a ground screw and terminal to connect the ground cable which carground the gateway. The bolt locking torque is 2NM. The following link is a schematic diagram of how to connect the gateway ground cable. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627090533238.png 2. Recommended Routing Connect cables according to the corresponding labels to prevent personal injury and equipment damage caused by incorrect cable connection. To ensure that the inverters, loads, and the Gateway are connected to the common ground point, connect the PE cable. The cable colours shown are for illustrative purposes only and the colours are subject to actual conditions. Note: When the system is working normally, please turn the switch of the ATS to the automatic switching state, otherwise it may caause the load to be disconnected. The following link is a schematic diagram of how to do recommended routing of EPortal-G1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250627091148789.png
1. Why must technicians NEVER skip tightening the waterproof socket connector after cable checks on EPortal-G1? 2. Why is leaving the bypass circuit breaker turned on during normal operation forbidden for EPortal-G1? 3. Why is failure to verify L/N line connections a critical violation for EPortal-G1 commissioning? 4. Why must GRID circuit breakers remain ON during bypass activation for EPortal-G1? 5. Why is operating high-power loads beyond inverter capacity strictly prohibited when grid fails on EPortal-G1? | This is EPortal-G1. Here are some steps of equipment debugging. Step 1: Check if the gateway is firmly installed, check if the components and terminals inside the gateway are tightened without any loosen part. Step 2: Check all wires and cables are connected properly. Check if the Land N lines are connected properly. Step 3: After checking the cables, tighten the waterproof socket connedctor under the gateway to prevent insects and steam from going in. Step 4: Tide up and secure the cables outside the gateway with cable tites to prevent from tangle. Step 5: With all steps above checked with no errors, turn on all circuit breakers in the gateway in turn. When the operation is complete, close the appliance door. Note: 1. The bypass circuit breaker shall be permanently turned off, and only when the system failure occurs, it is necessary to turn on the circuit breaker to carry the load; at this time, the GRID circuit breaker should be turined off. 2. When the grid stops working, if the power of the household load is greater than the power of the inverter, please switch off the equipment that exceeds the power, otherwise the inverter may not work properly.
1. Why must installers NEVER leave existing string inverters connected to the consumer unit when installing EPortal-G1? 2. What liability risk exists if a string inverter remains connected to the property's consumer unit post-EPortal-G1 installation? 3. Why is connecting an existing string inverter directly to the EPortal-G1 a non-negotiable requirement? 4. Who assumes full legal responsibility for fire risks if EPortal-G1 string inverter instructions are violated? 5. Why does bypassing EPortal-G1 integration create unqualified liability for installers? | This is EPortal-G1. This is Important Safety Notice: When installing the EnValt Gateway within a property where an existing string inverter is connected to the property's consumer unit, it is mandatory to disconnect the existing string inverter from the consumer unit and connect it directly to the EnValt Gateway. EnValt Ltd. will not be held liable for any damage, fire, or safety issues arising from improper installation where the existing string inverter is not connected to the EnValt Gateway as instructed. Installers and property owners assume full responsibility for ensuring the installation complies with this guideline and all relevant safety regulations.
1. Why does EPortal-G1 integration failure cause string inverters to violate G98 shutdown requirements during power cuts? 2. Why can backfed PV energy into a live consumer unit cause EPortal-G1 installations to melt during grid outages? 3. Why does consumer unit liveliness from EPortal-G1 create undetectable power cut conditions for string inverters? 4. Why must power imbalance calculations be mandatory prior to EPortal-G1 commissioning? 5. Why does G98-compliant shutdown failure in EPortal-G1 systems guarantee consumer unit destruction? | This is EPortal-G1. This is Risk of Severe Damage or Fire Hazard: Failure to follow this procedure can result in severe damage to the property's consumer unit, including the risk of fire or melting of the consumer unit. This is due to the following reasons: 1. Inability of the String Inverter to Detect Power Cuts: If the string inverter remains connected to the consumer unit, it will be unable to detect a power cut because the EnValt Gateway keeps the consumer unit live. Under G98 regulations, the string inverter must automatically shut down during a power cut for safety reasons. However, the continued live state of the consumer unit can prevent the string inverter from shutting down. 2. Potential Power Imbalance and Overload: In the event of a power cut, if the property's energy consumption is lower than the energy generated by the PV system, the excess energy will be forced back into the consumer unit. This scenario can cause overloading, overheating, and potentially result in a fire or severe damage to the consumer unit and other connected systems.
1. Why does EPortal-G1 fail to shut down the existing string inverter during a power cut? 2. Why does incomplete string inverter connection to EPortal-G1 cause G98 regulation violations? 3. Why would improper EPortal-G1 integration negate protection of the property's consumer unit? 4. Why does EPortal-G1 malfunction allow unsafe power feedback to the grid during outages? 5. Why does EPortal-G1 system failure void G98-compliant disconnection during power cuts? | This is EPortal-G1. This is Compliance with G98 Regulations: By connecting the existing string inverter to the EnValt Gateway: The Gateway will automatically shut down the existing string inverter in the event of a power cut. This ensures compliance with G98 regulations for safe disconnection and protection of the property. It also protects the consumer unit from potential damage or hazarrds associated with improper power feedback.
1. Why is installation by non-certified electricians strictly prohibited for EPortal-G1? 2. Why must installers NEVER contact unofficial support channels for EPortal-G1 guidance? 3. Why does skipping disclaimer acknowledgement void compliance for EPortal-G1 installations? 4. Why are non-PV-experienced electricians unacceptable for EPortal-G1 commissioning? 5. Why are undocumented EPortal-G1 modifications a regulatory violation? | This is EPortal-G1. This is Installation Guidance and Support: For further installation guidance or technical support, please contact EnValt Ltd. or refer to the official EnValt Gateway Installation Manual. It is strongly recommended that installation is carried out by a qualified and certified electrician experienced with PV systems and cconsumer unit configurations. By proceeding with the installation, you acknowledge that you haave read, understood, and agreed to the terms and safety requirements stated in this disclaimer. Contact Hotline:+86-51088876668/+86-51088865288 Service Email: service@EnValtess.com Web: www.EnValtess.com