## Sheet1
问题 | 答案
1. What does FX-12K-SL inverter consist of? 2. Can u make a basic introduction of FX-12K-SL inverter? 3. Can u show me a schematic diagram of FX-12K-SL inverter's operational status? | This is FX-12K-SL inverter. It's a new type of solar energy storage inverter which is integrated with solar energy storage, utility charging and energy storage, AC sine wave output. It adopts DSP control and features high response speed, reliability, and industrial standard through an advanced control algorithm. The following link is a schematic diagram of its operational status. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617154003848.png
1. What's FX-12K-SL inverter's feature? | This is FX-12K-SL inverter. Its features can be listed as follows. 1. Supports lead acid battery and li-ion battery connections. 2. With a dual activation function when the li-ion battery is dormant; either mains/photovoltaic power supply access can trigger the activation of the li-ion battery. 3. Support single-phase pure sine wave output. 4. Supports four different voltage levels of 200/208/220/230/240Vac per phase. 5. Supports two solar inputs and simultaneous tracking of two solar maximum power charging/carrying capacity functions. 6. Dual MPPT with 99.9% efficiency and maximum 22A current in a single circuit, perfectly adapted to high power modules. 7. 2 charging modes are available: solar only, mixed mains/PV charging. 8. With the time-slot charging and discharging setting function, you can set the time period for cutting in/out of mains charging and switch the time period between battery discharging and mains bypass power. 9. Energy saving mode function to reduce no-load energy losses. 10. With two output modes of utility bypass and inverter outputt, with uninterrupted power supply function. 11. LCD large screen dynamic flow diagram design, easy to understand the system data and operation status. 12. 360° protection with complete short circuit protection, overcurrent protection, over under voltage protection, overload protection, backfill protection, etc. 13. Support CAN, USB, and RS485 communication. supply mode.
1. What does a complete system of FX-12K-SL inverter consist of? 2. Can u show me FX-12K-SL inverter's system application scenario? | This is FX-12K-SL inverter. A complete system consists of the following components: PV modules: converts light energy into DC energy, which can be used to charge the battery via an inverter or directly inverted into AC power to supply the load. Utility grid or generator: connected to the AC input, it can supply the load and charge the battery at the same time. The system can also operate generally without the mains or generator when the battery and the PV module power the load. Battery: The role of the battery is to ensure the regular power supply of the system load when the solar energy is insufficient and there is no mains power. Home load: Various household and office loads can be connectted, including refrigerators, lamps, televisions, fans, air conditioners, and other AC loads. Inverter: The energy conversion device of the whole system. The actual application scenario determines the specific system wiring method. The following link is a schematic diagram of FX-12K-SL inverter's system application scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617155409190.png
1. What does 1 refer to on FX-12K-SL inverter's review? 2. What does 2 refer to on FX-12K-SL inverter's review? 3. What does 3 refer to on FX-12K-SL inverter's review? 4. What does 4 refer to on FX-12K-SL inverter's review? 5. What does 5 refer to on FX-12K-SL inverter's review? 6. What does 6 refer to on FX-12K-SL inverter's review? 7. What does 7 refer to on FX-12K-SL inverter's review? 8. What does 8 refer to on FX-12K-SL inverter's review? 9. What does 9 refer to on FX-12K-SL inverter's review? 10. What does 10 refer to on FX-12K-SL inverter's review? 11. What does 11 refer to on FX-12K-SL inverter's review? 12. What does 12 refer to on FX-12K-SL inverter's review? 13. What does 13 refer to on FX-12K-SL inverter's review? 14. What does 14 refer to on FX-12K-SL inverter's review? 15. What does 15 refer to on FX-12K-SL inverter's review? 16. What does 16 refer to on FX-12K-SL inverter's review? 17. What does 17 refer to on FX-12K-SL inverter's review? 18. What does 18 refer to on FX-12K-SL inverter's review? 19. What does 19 refer to on FX-12K-SL inverter's review? 20. What does 20 refer to on FX-12K-SL inverter's review? | This is FX-12K-SL inverter. 1 refers to LED Indicators. 2 refers to LCD screen. 3 refers to Touchable key. 4 refers to PV1 terminals. 5 refers to PV2 terminals. 6 refers to Generator terminals (L+N). 7 refers to Load terminals (L+N). 8 refers to Utility terminals (L+N). 9 refers to USB-B port. 10 refers to WIFI port. 11 refers to RS485 port. 12 refers to CAN port. 13 refers to External CT port. 14 refers to Dry contact. 15 refers to Parallel communication B port. 16 refers to Parallel communication A port. 17 refers to Battery terminal. 18 refers to PV circuit breaker. 19 refers to ON/OFF rocker switch. 20 refers to USB-A port. The following link is a schematic diagram of FX-12K-SL inverter's review which introduces its structure, including front and bottom panels.. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617161128808.png
1.Can u show me a schematic diagram of FX-12K-SL inverter's dimension drawings? | This is FX-12K-SL inverter. The following link is a schematic diagram about its dimension drawings from front, side, top and bottom views. On these pictures, we can see some data about its length, width and so on. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617161850025.png
1. Which factor do i need to take consideration into when I select the mount location of FX-12K-SL inverter? 2. Can u show me a schematic diagram about details of the heat dissipation space when selecting the mount location of FX-12K-SL inverter? 3. Do u have any temperature requirements when selecting the mount location of FX-12K-SL inverter? | This is FX-12K-SL inverter. It can be used outdoors (protection class IP65). When selecting the mount location, u need to take these factors into consideration. 1. Choose the solid wall to install the inverter. 2. Mount the inverter at eye level. 3. Adequate heat dissipation space must be provided for the inverter. 4. The ambient temperature should be between-25~60°C (-13~140°F) to ensure optimal operation. The following link is a schematic diagram which shows us details about heat dissipation space when selecting the mount location. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617162206117.png
1. Can i install FX-12K-SL inverter where highly flammable materials are near by? 2. Can i install FX-12K-SL inverter in potential explosive areas? 3. Can i install FX-12K-SL inverter with lead-acid batteries in a confined space? 4. Can i install FX-12K-SL inverter in direct sunlight? 5. Can i install or use FX-12K-SL inverter in a humid environment? | This is FX-12K-SL inverter. Here is 'Danger' and 'Caution' when locating the product. DANGER: Do not install the inverter where highly flammable materials are near by. Do not install the inverter in potential explosive areas. Do not install the inverter with lead-acid batteries in a confined space. CAUTION: Do not install the inverter in direct sunlight. Do not install or use the inverter in a humid environment.
1. What's the size of expansion screws in mounting FX-12K-SL inverter? 2. Can u show me a schematic diagram about screws, electric drills, size and FX-12K-SL inverter in mounting? | This is FX-12K-SL inverter. When Mounting the inverter, u need to punch 4 mounting holes in the wall with an electric drill accorrding to the specified size, and insert 4 M8*60 expansion screws above. Here are pictures about screws, electric drills, size and inverter in mounting. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617163157372.png
1. What do i need to use if i want to remove the terminal protection cover of FX-12K-SL inverter? | This is FX-12K-SL inverter. U can use a screwdriver to remove the terminal protection cover and anti-insect net. Here are pictures showing u where the terminal protection cover is and the bottom panel of the product. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617163348008.png
1. What should i notice if i use FX-12K-SL inverter in areas with poor air quality? | This is FX-12K-SL inverter. When using the device in areas with poor air quality, the fan cover is easily blocked by air particles. Please disassemble and clean the fan periodically to avoid affecting the internal air flow rate of the inverter, which may trigger an over-temperature protection fault (19/20 fault) affecting the use of the power supply and the service life of the inverter.
1. In FX-12K-SL inverter, what's the voltage between live and neutral wires in AC output port? | This is FX-12K-SL inverter. It has live and neutral wires and the voltage between them is 230V. The following link is a schematic diagram about AC output port and AC voltage sine curve illustration. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617164748078.png
1. Can users change the output mode and output voltage by setup menu of FX-12K-SL inverter? 2. What's the output voltage range of FX-12K-SL inverter? | This is FX-12K-SL inverter. Here's a "NOTICE". Users can change the output phase mode and output voltage by setup menu. The output voltage can be set from 200V to 240V.
1. Can u show me a schematic diagram about FX-12K-SL inverter's single-phase mode? | This is FX-12K-SL inverter. The following link is a schematic diagram about its single-phase mode. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250617165659734.png
1. What's the cable diameter requirement in PV input of FX-12K-SL inverter? 2. What's the Max. PV input current requirement of FX-12K-SL inverter? 3. What's the circuit breaker spec requirement in PV input of FX-12K-SL inverter? | This is FX-12K-SL inverter. In PV INPUT, the Cable Diameter is 5mm²/10AWG. Max. PV Input Current is 22A. Circuit Breaker Spec is 2P-25A.
1. What's the cable diameter requirement in AC input of FX-12K-SL inverter? 2. What's max input current requirement in generator of FX-12K-SL inverter? 3. What's circuit breaker spec requirement in generator of FX-12K-SL inverter? | This is FX-12K-SL inverter. In AC INPUT, the Cable Diameter is 13mm²/6AWG (L/N). Max. Max input current is 63A. Circuit Breaker Spec is 2P-63A.
1. What's cable diameter requirement in generator of FX-12K-SL inverter? 2. What's max input current requirement in generator of FX-12K-SL inverter? 3. What's circuit breaker spec requirement in generator of FX-12K-SL inverter? | This is FX-12K-SL inverter. In Generator, the Cable Diameter is 13mm²/6AWG (L/N). Max. input current is 63A. Circuit Breaker Spec is 2P-63A.
1. What's cable diameter requirement in battery of FX-12K-SL inverter? 2. What's max battery current requirement of FX-12K-SL inverter? 3. What's circuit breaker spec requirement in battery of FX-12K-SL inverter? | This is FX-12K-SL inverter. In Battery, the Cable Diameter is 54mm²/0AWG. Max. Battery Current is 270A. Circuit Breaker Spec is 2P-300A.
1. What's output model in AC output of FX-12K-SL inverter? 2. What's the cable diameter requirement in AC output of FX-12K-SL inverter？ | This is FX-12K-SL inverter. In AC OUTPUT, output model is single phase. Cable Diameter is 13mm²/6AWG (L/N). Circuit Breaker Spec is 2P-63A.
1. How much cable insulation should be stripped off for the connection of FX-12K-SL inverter? 2. What tool is required to prepare the cable for termination of FX-12K-SL inverter? 3. Which additional component must the user provide to secure the cable of FX-12K-SL inverter? | This is FX-12K-SL inverter. The following link is a notice about reference wire diameter according to different distances between the PV array and the inverter or between the inverter and the battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250618092039609.png PV INPUT, AC INPUT, AC OUTPUT 1. Use a stripper to remove the 6~8mm insulation of the cable. 2. Fixing a ferrule at the end of the cable. (ferrule needs to be prepared by the user). BATTERY 1. Use a stripper to remove the 6~8mm insulation of the cable. 2. Fixing cable lugs that supply with the box at the end of the cable. The wire diameter is for reference only. If the distance between the PV array and the inverter or between the inverter and the battery is long, using a thicker wire will reduce the voltage drop and improve the performance of the system.
1. How to connect the live, neutral and ground wires in GRID&LOAD&GEN connection of FX-12K-SL inverter? 2. What's DANGER in GRID&LOAD-GEN connection of FX-12K-SL inverter? | This is FX-12K-SL inverter. We should connect the live, neutral and ground wires in GRID&LOAD&GEN connection according to the calbles' position and order shown in the diagram below. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250618092458499.png In GRID&LOAD&GEN connection, there's some DANGER. 1. Before connecting AC inputs and outputs, the circuit breaker must be opened to avoid the risk of electric shock and must not be operated with electricitty. 2. Please check that the cable used is sufficient for the requirements, too thin, poor quality cables are a serious safety hazard. The following link is a diagram about "DANGER" in its GRID&LOAD&GEN connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250618092816130.png
1. In battery connection of FX-12K-SL inverter, how to connect the positive and negative cable of the battery? | This is FX-12K-SL inverter. In its battery connection, we should connect the positive and negative cable of the battery according to the diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250618093027404.png
1. Must I open the circuit breaker in battery connection of FX-12K-SL inverter? Why? 2. What will happen to FX-12K-SL inverter if I connect the positive and negative terminals of the battery incorrectly? | This is FX-12K-SL inverter. There is DANGER in its battery connection. 1. Before connecting battery, the circuit breaker must be opened to avoid the risk of electric shock and must not be operated with electricity. 2. Make sure that the positive and negative terminals of the battery are connected correctly and not reversed, otherwise the inverter may be damaged. 3. Please check that the cable used is sufficient for the requirements, too thin, poor quality cables are a serious safety hazard. The following link is a diagram about "DANGER" in battery connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250613135858466.png
1. In PV connection of FX-12K-SL inverter, how to connect the positive and negative wires of the two strings of PV? | This is FX-12K-SL inverter. In PV connection, u should connect the positive and negative wires of the two strings of PV according to the diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619102600072.png
1. What's the Max. Open Circuit Voltage of FX-12K-SL inverter? 2. Can open circuit voltage of the PV modules in series exceed the Max. Open Circuit Voltage of FX-12K-SL inverter? | This is FX-12K-SL inverter. In PV connection, there's DANGER. 1. Before connecting PV, the circuit breaker must be opened to avoid the risk of electric shock and must not be operated with electricity. 2. Please make sure that the open circuit voltage of the PV modules in series does not exceed the Max. Open Circuit Voltage of the inverter (this value is 500V), otherwise the inverter may be damaged.The following link is a diagram about "DANGER" in PV connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250613140524919.png
1. Can u show me a schematic diagram about FX-12K-SL inverter's dry contact connection? | This is FX-12K-SL inverter. In dry contact connection, use a small screwdriver to push back the direction indicated by the arrow, then insert the communication cable into the dry junction port. (Communication cable dianheter 0.2~1.5mm²). The following link is a schematic diagram about its dry contact connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619103559422.png
1. In the grounding connection of FX-12K-SL inverter, must the grounding terminal be connected to the grounding bar? 2. Can u show me a schematic diagram about FX-12K-SL inverter's grounding connection? | This is FX-12K-SL inverter. In grounding connection, please make sure the grounding terminal connect to the Grounding Bar. The following link is a schematic diagram about its grounding connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619103730500.png
1. In FX-12K-SL inverter's grounding connection, what's the exact diameter of grounding cable？ | This is FX-12K-SL inverter. In its grounding connection, there's a notice. The notice says that the grounding cable should have a diameter of not less than 4 mm² and be as close as possible to the grounding point.
1. What's the steps of final assembly of FX-12K-SL inverter? | This is FX-12K-SL inverter. After ensuring that the wiring is reliable and the wire sequeInce is correct, install the terminal protection cover in place. Then is our final assembly. Step 1: Close the circuit breaker of the battery. Step 2: Press the rocker switch on the bottom of inverter, the screen and indicators light up to indicate that the inverter has been activated. Step 3: Sequential close of the circuit breakers for PV, AC inpuut and AC output. Step 4: Start the loads one by one in order of power from small to large.
1. Can u show me a schematic diagram of FX-12K-SL inverter's parallel communication line? | This is FX-12K-SL inverter. And this is an introduction of the inverter parallel: 1. Up to six units connected in parallel. 2. When using the parallel operation function, the following connecting lines (package accessories) shall be firmly and reliably connected. The following link is a schematic diagram about its parallel communication line. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619104341073.png
1. In PV connection of FX-12K-SL inverter's PV connection, what are precautions for connecting the parallel connecting lines? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. In PV connection, when connected in parallel, the PV arrays of each machine must be independent and the PV arrays of PV1 and PV2 of each machine must also be independent.
1. In battery wiring of FX-12K-SL inverter, what are precautions for connecting the parallel connecting lines? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. In battery wiring, parallel connection in single or three-phase: ensure that all solar storage inverters are connected to the same battery, with BAT + connected to BAT + , BAT - Connected to BAT -, and that the connection is correct with the same wiring length and line diameter before power on, so as to avoid the abnormal operation of parallel system output caused by wrong connection.
1. In load wiring of FX-12K-SL inverter, what are precautions for connecting the parallel connecting line? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. In LOAD wiring, parallel connection in single phase: ensure L-to-L, N-to-Naind PE-to-PE connection for all solar storage inverters, and that the connection is correct with the same wviring length and line diameter before power on, so as to avoid the abnormal operation of parallel system output caused by wrong connection. Parallel connection in three-phase: ensure N-to-N and PE-to-PE connection for all solar storage inverters. The L lines of all inverters connected to the same phase need to be connected together. But L lines of different phases cannot be joined together. Other connection precautions are the same as parallel connection in single phase. For specific wiring, please refer to 2.4.4 Wiring Diagram.
1. In grid wiring of FX-12K-SL inverter, what are precautions for connecting the parallel connecting lines? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. In GRID wiring, Parallel connection in single phase: ensure L-to-L, N-to-N and PE-to-PE connection for all solar storage inverters, and that the connection is correct with the same wiring length and line diameter before power on so as to avoid the abnormal operation of parallel system output casused by wrong connection. Meanwhile, it is not allowed to have multiple different AC source inputs to avoid damage to the external equipment of the inverter. The consistency and uniqueness of AC source input shall be ensured. Parallel connection in three-phase: ensure N-to-Nand PE-to-PE connection for all solar storage inverters. The L lines of all inverters connected to the same phase need to bee connected together. But L lines of different phases cannot be joined together. Other connectionprecautions are the same as parallel connection in single phase. For specific wiring, please refer to 2.4.4Wiring Diagram.
1. In the wiring of parallel communication line of FX-12K-SL inverter, what are precautions for connecting the parallel connecting lines? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. In the wiring of parallel communication line, our parallel communication cable is a shielded 10Pin networlk connection cable, which can be used for single-phase or three-phase parallel connection. Each machine must be connected with one out and one in. This means that the machine "Parallel A" is connected to the machine to be parallelized "Parallel_B", and that the machine "Parallel A" is not allowed to connect to the "Parallel B". "Parallel B" or "Parallel A" is connected to the machine to be parallelized "Parallel_A". At the same time, the parallel communication cable of each machine should be fastened with 10Pin network connection cable to avoid disconnection or poor contact of the parallel communication cable, which may cause abnormal operation or damage to the system output.
1. After the system of FX-12K-SL inverter is wired, if a new inverter needs to be connected, what i should make sure to disconnect? | This is FX-12K-SL inverter. And there are some precautions for connecting the parallel connecting lines. Before and after connecting the system, please check the following system wiring diagrams in detail to ensure that all wiring is correct and reliable before powering on. After the system is wired, powered on and in normal operation, if a new inverter needs to be connected, make sure to disconnect the battery input, PV input, AC input and AC output, and that all solar storage inverters are powered off before reconnecting into the system.
1. When FX-12K-SL inverter works independently, how to set "single phase parallel" on the screen? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The parallel communication line of the solar storage inverter needs to be locked with screws after connecting in single phase. The parallel mode needs to be set as "single phase parallel" for each inverter. The following link is a schematic diagram about how to set "single phase parallel" on inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250613153038491.png
1. How to connect two single-phase FX-12K-SL inverters in parallel working as a big single-phase inverter? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The following link is a schematic diagram about two single-phase inverters connected in parallel to each other. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619111634801.png
1. How to connect three single-phase FX-12K-SL inverters in parallel working as a big single-phase inverter? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The following link is a schematic diagram about three single-phase inverters connected in parallel to each other. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619111758871.png
1. How to connect four single-phase FX-12K-SL inverters in parallel working as a big single-phase inverter? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The following link is a schematic diagram about four single-phase inverters connected in parallel to each other. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619111933189.png
1. How to connect five single-phase FX-12K-SL inverters in parallel working as a big single-phase inverter? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The following link is a schematic diagram about five single-phase inverters connected in parallel to each other. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619112146742.png
1. How to connect six single-phase FX-12K-SL inverters in parallel working as a big single-phase inverter? Can u show me a schematic diagram? | This is FX-12K-SL inverter. The following link is a schematic diagram about six single-phase inverters connected in parallel to each other. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619112250000.png
1. What is the output phase voltage of FX-12K-SL inverter connected in parallel in three phase? 2. How to set P1, P2, P3 on the screen of FX-12K-SL inverter connected in parallel in three phase? Can u show me a schematic diagram? 3. What is the line voltage between the live wire L1 in phase 1 and the live wire L2 in phase 2 of FX-12K-SL inverter? | This is FX-12K-SL inverter connected in parallel in three phase.The parallel communication line and current sharing detection line of the solar storage inverter need to be locked with screws after connecting. We need to set parellel operation modes in three phase: All inverters in P1 must be set as [three phase A]; All inverters in P2 must be set as [three phase B]; All inverters in P3 must be set as [three phase C]. The following link is a schematic diagram about how to set P1, P2, P3 on the screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250613160601607.png The output phase voltage is 230Vac. At present the line voltage between the live wire L1 in phase 1 and the live wire L2 in phase 2 is 230*1.732 = 398Vac, and similarly the line voltage.
1. How to connect three single-phase FX-12K-SL inverters in parallel to form a three-phase system? | These are three FX-12K-SL inverters connected in parallel in three phase. It is 1+1+1 system which means each phase has one inverter. The following link is a schematic diagram about "1+1+1 system". https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619113036804.png
1. How to connect four single-phase FX-12K-SL inverters in parallel to form a three-phase system? | These are four FX-12K-SL inverters connected in parallel in three phase. It is 2+1+1 system which means in phase 1, two inverters are connected together and there is one inverter in phase 1 and phase 2 respectively. The following link is a schematic diagram about how to connect four units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619132454715.png
1.How to connect five single-phase FX-12K-SL inverters in parallel to form a three-phase system? | These are five FX-12K-SL inverters connected in parallel in three phase. It has two types of connection. 1. 3+1+1 system. In phase 1, three inverters are connected together and there is one inverter in phase 2 and phase 3 respectively. The following link is a schematic diagram about one way to connect five units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619132626011.png 2. 2+2+1 system. In phase 1 and phase 2, two inverters are connected together and in phase 3, there is one inverter. The following link is a shcematic diagram about one way to connect five units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619132741567.png
1. How to connect six single-phase FX-12K-SL inverters in parallel to form a three-phase system? | These are six FX-12K-SL inverters connected in parallel in three phase. It has three types of connection. 1. 2+2+2 system. In phase 1, phase 2 and phase 3, there are two inverters connected together respectively. The following link is a schematic diagram about one way to connect six units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133029197.png 2. 3+2+1 system. In phase 1, there are three inverters connected together. In phase 2, there are two inverters connected together. In phase 3, there is one inverter. The following link is a shcematic diagram about one way to connect six units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133104691.png 3. 4+1+1 system. In phase 1, there are four inverters connected together. In phase 2 and phase 3, there is one inverter respectively. The following link is a shcematic diagram about one way to connect six units in three phase. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133137889.png
1. What do I need to notice in FX-12K-SL inverter connected in parallel in three phase? | This is FX-12K-SL inverter connected in parallel in three phase. Below are some notes about it. 1) Before starting up and running, please check whether the connection was correct to avoid any abnormalities in the system. 2) All wiring must be fixed and reliable to avoid wire drop during use. 3) When the AC output is wired to the load, it shall be properly wired according to the requirements of the electrical load equipment to avoid damage to the load equipmeent. 4) Setting item "output phase voltage setting" needs to be set consistently or only for the master. When paralleling, the voltage set by the master will prevail, and the masster will be forced to rewrite the rest of the slaves to be consistent. This option can be set in standby mode only. 5) Machine factory default for single machine mode, if you use parallel or three-phase function, you need to set the "Parallel mode" item parameters through the screen. The setting method is: power on one machine at a time, the rest of the machine off, and then set the "Parallel mode" item parameters according to the site system operation mode. After this machine isset successfully, turn off the machine switch and wait for the machine to be powered down, then set the rest of the machines in turn until all machines are set, and then all machines are powered up again at the same time and enter the working state. 6) After the system runs, the output voltage is measured correctly, and then the load setting is connected.
1. What does FX-12K-SL inveter's operation and display panel consist of? | This is FX-12K-SL inverter. The following link is a schematic diagram of its operation and display panel which includes 1 LCD screen, 3 indicators and 4 touchable keys. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133515195.png
1. What do 4 keys refer to respectively on FX-12K-SL inverter's operation and display panel? | This is FX-12K-SL inverter. The following link is a schematic diagram of its operation and display panel which includes 1 LCD screen, 3 indicators and 4 touchable keys. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133515195.png From left to right, 4 keys respectively mean "To enter/exit the setting menu", "To last selection", "To next selection" and "To confirm/enter the selection in setting menu". The following link is a diagram about the 4 keys. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133834768.png
1. When the red indicator flashes on FX-12K-SL inverter's operation and display panel, what does it mean? 2. When the yellow indicator is continued on FX-12K-SL inverter's operation and display panel, what does it mean? 3. When the yellow indicator flashes on FX-12K-SL inverter's operation and display panel, what does it mean? 4. When the green indicator is continued on FX-12K-SL inverter's operation and display panel, what does it mean? 5. When the green indicator flashes on FX-12K-SL inverter's operation and display panel, what does it mean? | This is FX-12K-SL inverter. The following link is a schematic diagram of its operation and display panel which consists of 1 LCD screen, 3 indicators and 4 touchable keys. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133515195.png From up to down, three indictors are "FAULT", "CHARGE" and "AC/INV". "FAULT" indicator is red. If it flashes, that means "error occurs". "CHARGE" indicator is green. If it's continued, it means "charging complete". If it flashes, that means "charging". "AC/INV" indicator is yellow. If it's continued, that means "utility grid by-pass output". If it flashes, that means "inverter output". The following link is a diagram about the three indicator. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134342639.jpg
1. On FX-12K-SL inverter's display panel's home page, what does the middle icon mean? 2. On FX-12K-SL inverter's odisplay panel's home page, where can i find history data? 3. If i want to do more settings on FX-12K-SL inveter's display panel, what should i do? | This is FX-12K-SL inverter. The following link is a schematic diagram of its operation and display panel which consists of 1 LCD screen, 3 indicators and 4 touchable keys. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619133515195.png On its display panel, there are many icons. On home page, we can see "Solar panel", "Load", "Battery", "Grid or Generator" icons. The middle icon shows whether the inverter is working. And we can also see energy direction and BMS communicate status. If we press "History" icon, we can then see history data. If we want to do more settings, we can press "Setting" icon. The following link is a schematic diagram of its display panel's home page and a table that illustrates the meaning of each icon. The following link is a schematic diagram of its display panel's home page https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png and a table that illustrates the meaning of each icon. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134819322.png
1. On FX-12K-SL inverter's LCD home screen, what system data i can know? | This is FX-12K-SL inverter. On its LCD home screen, click the inverter icon, battery icon, mains icon, load icon and photovoltaic icon, then we can view the real-time data of the machine. The following link is a schematic diagram of its LCD screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png In system data, NO.1 is machine state. No.2 is MCU1 version. NO.3 is LCD version. NO.4 is MCU2 version. NO.5 is Outside Temperature. NO.6 is inverter voltage. NO.8 isSN. NO.9 is Min version number. NO.10 is Rated power. NO.11 is RS485 Address. NO.12 is Transformer temperature. NO.13 is inverter current. The following link is a diagram of its system data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619135825956.png
1. On FX-12K-SL inverter's LCD home screen, what battery data can i know? | This is FX-12K-SL inverter. On its LCD home screen, click the inverter icon, battery icon, mains icon, load icon and photovoltaic icon, then we can view the real-time data of the machine. The following link is a schematic diagram of its LCD screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png In battery data, NO.1 is SOC (Percentage of remaining battery capacity). NO.2 is Battery voltage. NO.3 is Battery current. NO.4 is Battery power (Battery charging and discharging power). NO.5 is Discharge current. NO.6 is BMS protocol. NO.7 is Battery type. NO.8 is Battery Charge Status. The following link is a diagram about its battery data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619140245519.png
1. On FX-12K-SL inverter's LCD home screen, what grid data can i know? | This is FX-12K-SL inverter. On its LCD home screen, click the inverter icon, battery icon, mains icon, load icon and photovoltaic icon, then we can view the real-time data of the machine. The following link is a schematic diagram of its LCD screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png In grid data, NO.1 is Voltage V. NO.2 is active power. NO.3 is Frequency. NO.4 is CT power. NO.5 is Current A. NO.6 is apparent power. NO.7 is Mains charging current. The following link is a diagram of its grid data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619140544651.png
1. On FX-12K-SL inverter's LCD home screen, what load data can i know? | This is FX-12K-SL inverter. On its LCD home screen, click the inverter icon, battery icon, mains icon, load icon and photovoltaic icon, then we can view the real-time data of the machine. The following link is a schematic diagram of its LCD screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png In load data, NO.1 is voltage. NO.2 is UPS load active power. NO.3 is Frequency. NO.4 is BUS Voltage. NO.5 is Current. NO.6 is UPS load apparent power. NO.7 is load rate. The following link is a diagram of its load data.https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619140802715.png
1. On FX-12K-SL inverter's LCD home screen, what PV data can i know? | This is FX-12K-SL inverter. On its LCD home screen, click the inverter icon, battery icon, mains icon, load icon and photovoltaic icon, then we can view the real-time data of the machine. The following link is a schematic diagram of its LCD screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png In PV data, NO.1 is PV1 voltage A. NO.2 is PV1 current A. NO.3 is PV1 power W. NO.4 is PV2 voltage V. NO.5 is PV2 current. NO.6 is PV2 power. NO.7 is Generate energy total (kWh). The following link is a diagram of its PV data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619142302243.png
1. What parameter can i know from "Display Setup" of "Basic Setup" on LCD home screen of FX-12K-SL inverter? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Basic Setup includes Display Setup, Time Setup, Password Setting (Password is required to access the Grid Settings and Advanced Settings. The following link is a schematic diagram of "Display" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619142926697.png On this interface, there are some parameter meanings. "Language" is "Currently only English". "RS485 Address" is "Display and current inverter RS485 address, range 1-254". "Screen always on" is "Selectable whether the screen is always on or not". "Beep" is "You can choose whether to enable the Beep alarm". "Screen brightening time" is "Setting range 0-60S". "Backlight brightness" is "0-100%". The following link is a diagram of specific parameter meanings on "Display" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619143204109.png
This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Basic Setup includes Display Setup, Time Setup, Password Setting (Password is required to access the Grid Settings and Advanced Settings. The following link is a schematic diagram of "Display" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619142926697.png On the "Time" interface , we can set "Year" "Month" "Day" "Hour" "Minute" and "Second". The following link is a schematic diagram of "Time" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619143959500.png
1. On the "Password Setting" interface on "Basic Setup" on LCD home screen of FX-12K-SL inverter, what is its default password? 2. On the "Password Setting" interface on "Basic Setup" on LCD home screen of FX-12K-SL inverter, how to change the password? 3. On the "Password Setting" interface on "Basic Setup" on LCD home screen of FX-12K-SL inverter, what's the password setting value range? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Basic Setup includes Display Setup, Time Setup, Password Setting (Password is required to access the Grid Settings and Advanced Settings. The following link is a schematic diagram of "Display" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619142926697.png On the "Password Setting" interface, we can input new password and then confirm it. Default password is "00000" and the password setting value range is 0-65535. The following link is a schematic diagram of its "Password Setting" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144130529.png
1. How many options are there under the Hybrid grid mode on the "Work Mode Setup" of FX-12K-SL inverter's LCD home screen? 2. What does "On grid" mean on the work mode on the LCD home screen of FX-12K-SL inverter? 4. What does "Limit Power to ups load" mean on the work mode on the LCD home screen of FX-12K-SL inverter? 5. What does "Limit Power to home load" mean on the work mode on the LCD home screen of FX-12K-SL inverter? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png Under Hybrid grid mode, there are three options. "On grid" means "Direct grid connection of excess PV energy". "Limit Power to ups load" means "Ups load backflow prevention, photovoltaic or battery energy is only for the ups load, excess energy will not be connected to the grid". UPS load is connected to the LOAD port of the machine. "Limit Power to home load" means "Home load anti-backflow, solar or battery energy is only supplied to the home load, excess energy will not be connected to the grid." Home Load is connected to the GRID port of the machine, requirres external CT for monitoring.
1. If i set FX-12K-SL inverter's PV energy manage as "First to Load" on the "Work Mode Setup" on LCD home screen, what's the PV power supply logic? 2. If i set FX-12K-SL inverter's PV energy manage as "First to Charging" on the "Work Mode Setup" on LCD home screen, what's the PV power supply logic? 3. If i set FX-12K-SL inverter's PV energy manage as "First to Grid" on the "Work Mode Setup" on LCD home screen, what's the PV power supply logic? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png Under PV energy manage, there are three options. When mixed grid mode is set to "Limit Power to ups load" or when CT is not connected, the following load refers to the ups load. When mixed grid mode is set to "Limit Power to home load/On grid" and CT is connected, the following load refers to the ups load plus the home load. "First to Load" means "PV power supply logic: load-charge-grid connection". "First to Charging" means "PV power supply logic: charge-load-grid connection". "First to Grid" means "PV power supply logic: load-grid connection-charge".
1. Can I select grid participation in battery charging on FX-12K-SL inverter's "Work Mode Setup" on LCD home screen settings? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png "Grid charging enable" refers to "Selectable grid participation in battery charging"
1. If i set FX-12K-SL inverter's battery energy manage as "standby" on "Work Mode Setup" on LCD home screen, what does it mean? 2. If i set FX-12K-SL inverter's battery energy manage as "battery to ups load" on "Work Mode Setup" on LCD home screen, what does it mean? 3. If i set FX-12K-SL inverter's battery energy manage as "battery to home load" on "Work Mode Setup" on LCD home screen, what does it mean? 4. If i set FX-12K-SL inverter's battery energy manage as "battery to grid sell" on "Work Mode Setup" on LCD home screen, what does it mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png Under Battery energy manage, there are four options. "Standby" means "The battery does not discharge, and the battery is discharged only when the working state is off the grid." "Battery to ups load" means "When the PV power is less than the UPS load power, the battery discharge is added." "Battery to home load" means "The battery can supply the power to Home load". "Battery to grid sell" means "The battery can supply the power to grid".
1. How many parallel modes do FX-12K-SL inverters have on its work mode setup? 2. How should i set parallel mode of FX-12K-SL inverter on its work mode setup? 3. What's the present line voltage between the live wire L1 in phase 1 and the live wire L2 in phase 2 of FX-12K-SL inverter ? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png Under Parallel mode, there are five options: "Stand-alone", "Single phase Parallel", "Three Phase A", "Three Phase B" and "Three Phase C". In Three-phase parallel connection setting, All machines in phase 1 must be set as [three phase A]. All machines in phase 2 must be set as [three phase B]. All machines in phase 3 must be set as [three phase C]. And the output voltage is 230Vac. At present the line voltage between the live wire L1 in phase 1 and the live wire L2 in phase 2 is 230*1.732 = 398Vac, and similarly the line voltage.
1. How many types of output phase voltage of FX-12K-SL inverter can i choose on the "work mode" interface on LCD home screen? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Work Mode, there are some parameters including Hybrid grid mode, PV energy manage, Battery energy manage, Parallel Mode and Output phase voltage. The following link is a schematic diagram of "work mode" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619144733194.png Under Output phase voltage, there are five options: 200V, 208V, 220V, 230V, 240V.
1. On FX-12K-SL inverter's "Peak Shaving" interface on "work mode setup" on LCD home screen, what does "Time charging/discharging enable" refer to? 2. On FX-12K-SL inverter's "Peak Shaving" interface on "work mode setup" on LCD home screen, what does "Stop SOC" refer to? 3. On FX-12K-SL inverter's "Peak Shaving" interface on "work mode setup" on LCD home screen, what does "Stop Volt" refer to? 4. On FX-12K-SL inverter's "Peak Shaving" interface on "work mode setup" on LCD home screen, what does "Max Power" refer to? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Work Mode Setup includes Work Mode and Peak Shaving. On Peak Shaving, there are some parameters, including Time charging/discharging enable, Start/End Time, Stop SOC, Stop Volt, Max Power, Grid charge and Generator. The following link is a schematic diagram of its "peak shaving" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619150448042.png "Time charging/discharging enable" refers to "Select whether to turn on timed charging and discharging". "Start/End Time" refers to "Setting the time period for timed charging and discharging". "Stop SOC" refers to "Setting the battery charging cut-off SOC value and the cut-offf SOC value for discharging during the timed charging and discharging time period (during BMS communication)". "Stop Volt" refers to "Setting the battery charging cut-off voltage value and discharging cut-off voltage value during the timed charging and discharging time period (wherthe BMS is not communicating)". "Max Power" refers to "Setting the battery charging power and discharging power during the timed charging and discharging time period". "Grid charge" refers to "When setting the timed charge, select the grid to charge the battery". "Generator" refers to "When setting the timed charge, select the generator to charge the battery".
1. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does HMI setting mean? 2. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does BMS protocol mean? 3. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does Inverter logic mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Type", there are some parameters including Battery chg. curr. limit (Valid for BMS communication), BMS comm. interface, Battery Temperature Compensation, Battery Type and Battery comm. protocol. The following link is a schematic diagram of its "Battery Type" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619151306160.png Battery chg. curr. limit (Valid for BMS communication) has three options. "HMI setting" means "Maximum battery charging current is limited according to the inverter battery charging current setting value". "BMS protocol" means "Maximum battery charging current is limited by tthe current limit value of the BMS". "Inverter logic" means "Maximum battery charging current is limited by the machine's derating logic".
1. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Disable" mean? 2. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "RS485" mean? 3. On "Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "CAN" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Type", there are some parameters including Battery chg. curr. limit (Valid for BMS communication), BMS comm. interface, Battery Temperature Compensation, Battery Type and Battery comm. protocol. The following link is a schematic diagram of its "Battery Type" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619151306160.png BMS comm. interface has three options, including "Disable", "RS485" and "CAN". "Disable" means "BMS does not communicate". "RS485" means "BMS RS485 communication function". "CAN" means "BMS CAN communication function".
1. On the"Battery Type" on "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Battery Temperature Compensation" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Type", there are some parameters including Battery chg. curr. limit (Valid for BMS communication), BMS comm. interface, Battery Temperature Compensation, Battery Type and Battery comm. protocol. The following link is a schematic diagram of its "Battery Type" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619151306160.png Battery Temperature Compensation means "Select whether to turn on temperature compensation".
1. On "Battery Type" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "USER" mean? 2. On "Battery Type" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "SLd" mean? 3. On "Battery Type" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "GEL" mean? 4. On "Battery Type" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "N13/N14" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Type", there are some parameters including Battery chg. curr. limit (Valid for BMS communication), BMS comm. interface, Battery Temperature Compensation, Battery Type and Battery comm. protocol. The following link is a schematic diagram of its "Battery Type" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619151306160.png Battery Type has seven options. "USER" means "User customizable to set all battery parameters". "SLd" means "Sealed Lead Acid Battery". "FLd" means "Open-ended lead-acid batteries". "GEL" means "gel lead-acid battery". "LFP 14/15/16" means "Li-FePO4/14/15/16, corresponding to Li-FePO4 14 string, 15 string, 16 string". "N13/N14" means "Ternary lithium batteries, corresponding to ternary lithium batteries 13 string, 14 string". "No battery" means "Without battery".
1. What battery communication protocols are supported in the "Battery Type" settings of the FX-12K-SL? 2. Which lithium battery brands are compatible with the FX-12K-SL when using the 485 communication protocol? 3. How do I set the BMS communication protocol for a EnValt lithium battery in the FX-12K-SL? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Type", there are some parameters including Battery chg. curr. limit (Valid for BMS communication), BMS comm. interface, Battery Temperature Compensation, Battery Type and Battery comm. protocol. The following link is a schematic diagram of its "Battery Type" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619151306160.png In BMS comm. protocol, when the BMS port selection setting item = 485 or CAN, you neeed to select the corresponding lithium battery manufacturer brand for communication: 485 protocol: WOW-HANCHU,PYL-PYL-PYLONTECH CAN protocol:16:UZE=HANCHU
1. On "Battery Manage" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Maximum chg. voltage" mean? 2. On "Battery Manage" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Batt volt. stop dchg" mean? 3. On "Battery Manage" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Batt volt low fault recovery" mean? 4. On "Battery Manage" on the "Battery Setup" interface on LCD home screen of FX-12K-SL inverter, what does "Batt voltage low fault" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png Battery Setup includes Battery Type, Battery Manage. On "Battery Manage", there are some parameters. The following link is a schematic diagram of its "Battery Manage" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619153839974.png "Maximum chg.voltage" refers to "When the battery is charging, the voltage reaches the valueto stop charging". "Batt. Recharging voltage" refers to "When the battery is fully charged, the inverter stops charging and resumes charging when the battery voltage falls below this voltage value. "Battery curr. stop chg." refers to "Charging stops when the charging current falls below this setting." "Stop discharge Voltage" refers to " When the battery is discharged, the voltage reaches the value and stops discharging." "Eod recovery voltage" refers to "When the battery low voltage disconnects the inverter output, the battery voltage needs to be greater than this setting to restore the battery iinverter AC output." "Battery under volt. alarm" refers to "Battery under-voltage alarm point, when the battery voltage is lower than judgment point, the under-voltage alarm will be reported and the output will not be turned off." "Maximum chg. current" refers to "Setting the amount of current when charging the battery." "Max. chg.curr.by Grid" refers to "When using mains charging, set the size of the battery mains charging current (the value is the battery current, DC)." "Bat.SOC stop chg." refers to "Charging will stop when the SOC value reaches this set point (effective when BMS communication is normal)." "stop.dchg.delay time" refers to "When the battery voltage reaches the 'Stop Discharge Voltage' setting, the inverter output is shut down with a delay." "Batt. SOC stop dchg." refers to "When the SOC value reaches this setting, an error 32 is reported and the inverter output is shut down (valid when BMS communication is normal)." "Batt SOC low alarm" refers to "SOC value up to this setting will report 30 faults. The inverter coutput will not shut down and the fault disappears if the SOC value exceeds 5% of the seet value. (Valid when BMS communication is normal)." "Batt.volt.stop dchg to grid" refers to "When the battery reaches the voltage value, it switches to the grid suupply." "Batt.soc.stop dchg to grid" refers to "When the battery reaches the SOC value, it is converted to mains power supply (effective for BMS communication)."
1. Does FX-12K-SL inverter have different grid standards? 2. On the "on grid setup" on LCD home screen of FX-12K-SL inverter, what does "Sell power Max" mean? 3. On the "on grid setup" on LCD home screen of FX-12K-SL inverter, what does "Buy power Max" mean? 4. On the "on grid setup" on LCD home screen of FX-12K-SL inverter, what does "Reactive Power over/under excited" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png To enter the on grid setup, we need to enter the password set by the user and the default password is "00000". On "Basic" interface, there are some parameters about Grid Standard, Grid Frequency, CT ratio, Sell power Max, Buy power Max, Zero-export Power, On-Grid Reactive Power, Reactive Power over/under excited, On Grid PF and Power factor over/under excited. The following link is a schematic diagram of its "Basic" interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619155446155.png The grid standard is different among countries. This following link can illustrate it further. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619155624233.png Grid Frequency is "Selection of local grid frequency, 50Hz/60Hz". CT ratio means "When connecting an external CT, enter the ratio on the CT speciffication". Sell power Max is "On grid power". Buy power Max is "Maximum power drawn from the grid. If the grid charging power + load power exceeds this setting, the machine reduces the charging power. (Setting range: 0 to rated power)". Zero-export power is "Error calibration power in the case of backflow prevention, recommended setting 20-100W".
1. On the "Generator" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Max charging current by gen." mean? 2. On the "Generator" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Generator rate power" mean? 3. On the "Generator" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Generator charging enable" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png To enter the advance setup, we need to enter the password set by the user and the default password is "00000". On the "Generator" interface, there are some parameters. "Max charging current by gen." means "Maximum battery charging current during generator charging". "Generator rate power" means "Setting the power of the generator up to the rated power of the inverter". "Generator charging enable" means "Setting whether the generator is charged or not". The following link is a schematic diagram of "Generator" interface on the advance setup. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619161707540.png
1. On the "Other" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "PE-N connect enable" mean? 2. On the "Other" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "PV Riso check enable" mean? 3. On the "Other" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Leakage curr. protection enable" mean? 4. On the "Other" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Power saving mode" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png To enter the advance setup, we need to enter the password set by the user and the default password is "00000". On the "Other" interface, there are some parameters. "PE-N connect enable" means "Enable automatic switching of PE-N connections". "PV Riso check enable" means "Enable PV insulation impedance detection". "Leakage curr. protection enable" means "Enable leakage current protection". "Power saving mode" means "After turning on the energy-saving mode, if the load is empty or lesthan 25W, the inverter output will be shut down after a delay of 5min; when the loaad is more than 40W, the inverter will start automatically". The following link is a schematic diagram of "Other" interface on the advance setup. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619162008076.png
1. On the "Restart" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Restore Factory Settings" mean? 2. On the "Restart" interface on the advance setup on LCD home screen of FX-12K-SL inverter, what does "Reboot Inverter" mean? | This is FX-12K-SL inverter. On its LCD home screen, we can click on the settings in the menu bar at the bottom of the screen to enter the setup interface, including the basic settings, work mode setup, battery setup, on grid setup, advanced setup of the five major setup items. The following link is a schematic diagram of its LCD home screen. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619134743096.png To enter the advance setup, we need to enter the password set by the user and the default password is "00000". On the "Restart" interface, there are some parameters. "Restore Factory Settings" means "Reset all inverter settings". "Reboot Inverter" means "Restart the inverter". The following link is a schematic diagram of "Restart" interface on the advance setup. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619162254241.png
1. FX-12K-SL inverter is equipped with a time-slot charging and discharging function, so what's the use of this function? 2. Where can users turn on/off the time-slot charging/discharging function of FX-12K-SL inverter? | This is FX-12K-SL inverter. It is equipped with a time-slot charging and discharging function, which allows users to set different charging and discharging periods according to the local peak and valley tariffs, so that the utility power and PV energy can be used rationally. When mains electricity is expensive, the battery inverter is used to carry the load; when the mains electricity is cheap, the mains electricity is used to carry the load and charge, whiich can help customers to save electricity costs to the greatest extent. The user can turn on/off the time-slot charging/discharging function in setup menu parameter 46 and 53 and set charging and discharging slot in parameter. The following link is a schematic diagram of the time-slot charging/discharging function. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619162607852.png With 3 definable periods, the user can freely set the mains charging/carrying time within the range of 00:00 to 23:59. During the time period set by the user, if PV energy is available, PV energy will be used first, and if PV energy is not available or insufficient, utility energy will be used as a supplement. With 3 definable time periods, users can freely set the battery discharge time within the range of 00:00 to 23:59. During the time set by the user, the inverter will give prijority to the battery inverter to carry the load, and if the battery power is insufficient, the inverter will automatically switch to mains power to ensure stable operation of the load.
1. Can u show me a schematic diagram of FX-12K-SL inverter's communication ports from bottom view? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom view. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png 9 refers to USB-B port. 10 refers to WIFI port. 11 refers to RS485 port. 12 refers to CAN port. 13 refers to External CT port. 14 refers to dry contact. 20 refers to USB-A port.
1. Which communication port should i use if i want to read and modify FX-12K-SL inverter's parameters? 2. Can u show me a schematic diagram of FX-12K-SL inverter's USB-B port? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png and 9 refers to USB-B port. The following link is a schematic diagram of its USB-B port. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619164126347.png The user can read and modify device parameters through this port by using the host software. Please contact us for the host software installation package if you require one.
1. When FX-12K-SL inverter's RS485-1 port is used to connect to the Wi-Fi/GPRS data acquisition module, what can i view via the mobile phone APP? 2. Can u show me a schematic diagram of FX-12K-SL inverter's WIFI port? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png and 10 refers to WIFI port. The following link is a schematic diagram of its WIFI port and 8 PIN ports and their definitions. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619164724677.png The RS485-1 port is used to connect to the Wi-Fi/GPRS data acquisition module, which allows the user to view the operating status and parameters of the inverter via the mobile phone APP.
1. Can u show me a schematic diagram of FX-12K-SL inverter's CAN port? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png and 12 refers to CAN port. The following link is a schematic diagram of its CAN port and 8 PIN ports and their definitions. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619165130387.png The CAN port is used to connect to the BMS of Liion battery.
1. Can u show me a schematic diagram of FX-12K-SL inverter's RS485 port? 2. What does FX-12K-SL inverter's RS485 port connect to? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png 11 refers to RS485 port. The following link is a schematic diagram of its RS485 port and 8 PIN ports https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619165344624.png and 8 PIN ports' definitions https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619165422068.png . The RS485 port is used to connect to the BMS of Liion battery. Pin4 and Pin5 are for CAN. Notice: If you need the inverter to communicate with the lithium batttery BMS, please contact us for the communication protocol or to upgrade the inverter to the corresponding software program.
1. Can u show me a schematic diagram of FX-12K-SL inverter's USB-A port? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png 20 refers to USB-A port. The following link is a schematic diagram of its USB-A port. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619171937576.png It is used to updated the LCD screen firmware.
1. What's FX-12K-SL inverter's CT direction? 2. What's the secondary output cable length of FX-12K-SL inverter's CT? 3. Can u show me a schematic diagram of HESS-S-12K-S inverter's external CT port? 4. Can u show me a schematic diagram of HESS-S-12K-S inverter's external CT port's 8 PIN ports and their definitions? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png and 13 refers to External CT port. The following link is a schematic diagram of external CT model connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620090617557.png The following link is a schematic diagram of its 8 PIN ports and their definitions. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620090748922.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620090826495.png The following link is a schematic diagram about Split CT Transformer(CT) dimension (mm). The secondary output cable length is 4m and the CT direction is "to inverter". https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620091115066.png
1. What's the functions of FX-12K-SL inverter's dry contact port? 2. What should i notice if i want to use the generator remote start/stop with FX-12K-SL inverter's dry contact? | This is FX-12K-SL inverter. The following link is a schematic diagram of its communication ports from bottom viewhttps://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250619163656935.png and 14 refers to dry contact. Dry contact port has 3 functions: 1. RSD power supply: PIN 1 is GND, PIN 2 is RSD 12V+. 2. Temperature sampling (reserved) : Pin 1 & Pin 5 can be used for battery temperature sampling compensation. 3. Generator remote start/stop: 6-7: NC 6-8:NO Remote generator shutdown: Pins 6 to 7 are normally closed,and pins 7 to 8 are normally open. (Pin 6/7/8 output 125Vac/1A,230Vac/1A,30Vdc/1A). The following link is a schematic diagram of dry contact port's 8 PIN ports. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620092833176.png Notice: If you need to use the remote start/stop function of the generator with dry contact, ensure that the generator has ATS and supports remote start/stop.
1. What are protection features of HESS-S-12K-S inverter? | This is FX-12K-SL inverter. It has some protection features and i will illustrate them as follows. 1. PV input current/power limiting protection: When the charging current or power of the PV array configuredd exceeds the PV input rated value, the inverter will limit the input power and charge at the rated. 2. PV input over-voltage: If the PV voltage exceeds the maximum value allowed by the hardware, the machine will report a fault and stop the PV bodost to output a sinusoidal AC wave. 3. PV night reverse current protection: At night, the battery is prevented from discharging through the PV module because the battery voltage is greater than the voltage of PV module. 4. AC input over-voltage protection: When the AC input voltage of each phase exceeds 280V, the mains charging will be stopped and switched to the inverter mode. 5. AC input under-voltage protection: When the AC input voltage of each phase below 170V, the utility charging will be stopped and switched to the inverter mode. 6. Battery over-voltage protection: When the battery voltage reaches the over-voltage cut-off point, the PV and the utility will automatically stop charging to preverht the battery from being overcharged and damaged. 7. Battery under-voltage protection: When the battery voltage reaches the under-voltage cut-off poirnt, the inverter will automatically stop the battery discharge to preveent damage from over-discharging the battery. 8. Battery over-current protection: After a period when the battery current exceeds that allowed by the hardware, the machine will switch off the output and stop discharging the battery. 9. AC output short-circuit protection: When a short-circuit fault occurs at the load output terminal the AC output is immediately turned off and turned on after 1 second. lf the output load terminal is still short-circuited after 3 attempts, the inverter must be manually restarted after first removing the short-circuit fault from the load before the normal output can be restored. 10. Heat sink over-temperature protection: When the internal temperature of the inverter is too high, the inverter will stop charging and discharging; when the temperature returns to normal, the inverter will resume charging and discharging. 11. Inverter over-load protection: After triggering the overload protection the inverter will resume output after 3 minutes, 5 consecutive overloads will switch off thbe output until the inverter is restarted. (102%<load<110%): alarm and output shutdown after 5min; (110%< load < 125%) : alarm and output shutdown after 10s. Load > 125% : alarm reported and output switched off after 5s. 12. AC output reverse: Prevents AC back flow from the battery inverter to the bypass AC input. 13. Bypass over-current protection: Built-in AC input over-current protection circuit breaker. 14. Bypass phase inconsistency protection: When the phase of the bypass input and the phase of the inverter split do not match, the inverter disables switching to the bypass output to prevent the load from dropping out or short-circuiting when switching to the bypass. 15. Charging short-circuit protection: When the external battery port is short-circuited in the PV or AC charging state, the inverter will protect and stop the output curreent. 16. Parallel connection error protection: In parallel operation, the equipment will be protected when thhe parallel line is lost. 17. Parallel battery voltage difference protection: In parallel operation, the equipment will be protected when the battery connection is inconsistent and the battery voltage is greatly different from that detected by the host. 18. Parallel AC voltage difference protection: In parallel operation, the equipment will be protected when the AC IN input connection is inconsistent. 19. Synchronization signal fault protection: The equipment will be protected when there is a fault inthe guidance signal between parallel buses, causing inconsistent behavior of each inverter.
1. What should i do if i want to maintain optimum and long-lasting working performance of FX-12K-SL inverter? | This is FX-12K-SL inverter. To maintain optimum and long-lasting working performancce, we recommend that the following items are checked twice a year. 1. Ensure that the airflow around the inverter is not blocked and remove any dirt or debris from the radiator. 2. Check that all exposed conductors are not damaged by sunlight, fricticon with other surrounding objects dry rot, insect or rodent damage, etc. The conductors need to be repaired or replaced if necessary. 3. Verify that the indications and displays are consistent with the operation of the equipment, note any faults or incorrect displays and take corrective action if necessarry. 4. Check all terminals for signs of corrosion, insulation damage, high temperatures or burning/discolouration and tighten terminal screws. 5. Check for dirt, nesting insects and corrosion, clean as required. Clean the insect screen regularly. 6. If the lightning arrester has failed, replace the failed arrester in time to prevent lightning damage to the inverter or other equipment of the user.
1. What's the "DANGER" in FX-12K-SL inverter's maintenance? | This is FX-12K-SL inverter. Here is "DANGER" in its maintenance. Make sure that the inverter is disconnected from all power sources and that the capacitors are fully discharged before carrying out any checks or operations to avoid the risk of electric shock.
1. Which type of damage of FX-12K-SL inverter ur company shall not be liable for? | This is FX-12K-SL inverter. The Company shall not be liable for damage caused by: 1. Damage caused by improper use or use in a wrong location. 2. Photovoltaic modules with an open circuit voltage exceeding the maximum permissible voltage. 3. Damage caused by the operating temperature exceeding the restricted operating temperature range. 4. Dismantling and repair of the inverter by unauthorised persons. 5. Damage caused by force majeure: damage during transport or handling of the inverter.
1. What's the rated output power of FX-12K-SL inverter output? 2. What's the max. peak power of FX-12K-SL inverter output? 3. What's the rated AC frequency of FX-12K-SL inverter output? | This is FX-12K-SL inverter. Here's a datasheet about it. When it comes to Inverter output, the rated output power is 12000W. Max. peak power is 24000W. Its rated output voltage is 230Vac (single phase) (200/208/220/240Vac settable). Load capacity of motors are 6HP. Rated AC frequency is 50/60Hz± 0.3Hz. Its waveform is pure sine wave. Switch time is 10ms (typical). After triggering the overload protection the inverter will resumee output after 3 minutes, 5 consecutive overloads will switch off the output until the inverter is restarted. (102%<load<125%): alarm and output shutdown after 5min; (125% < load < 150%): alarm and output shutdown after 10s. Load > 150% : alarm reported and output switched off after 5s. The following link is a diagram of inverter output data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620095153811.png
1. What's the power factor when it comes to FX-12K-SL inverter's AC OUT (on grid)? 2. What's rated AC out current when it comes to FX-12K-SL inverter's AC OUT (on grid)? | This is FX-12K-SL inverter. Here's a datasheet about it. When it comes to AC OUT (on grid), the rated output power is 12000W. Max.peak power is 12000VA. Power factor is 0.8 leading to 0.8 lagging. The rated voltage is 220/230Vac. Rated AC frequency is 50/60Hz. Rated AC out current is 52.2Aac. THD is <3%. The following link is a diagram of AC OUT data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620095400333.png
1. What's battery type of FX-12K-SL inverter? 2. What's FX-12K-SL inverter's battery's voltage range? 3. What's max.generator charging current of FX-12K-SL inverter's battery? | This is FX-12K-SL inverter. Here's a datasheet about it. When it comes to Battery, battery type is Li-ion / Lead-Acid / User Defined. The rated battery voltage is 48Vdc (minimum start-up voltage 44V). Voltage range is 40-60Vdc. Max. generator charging current is 60Adc. Max. grid charging current is 120Adc. Max. hybrid charging current is 200Adc. The following link is a diagram of battery data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620095619597.png
1. What's the max.PV array power of FX-12K-SL inverter? 2. What's max.voltage of open circuit when it comes to PV input of FX-12K-SL inverter？ | This is FX-12K-SL inverter. Here's a datasheet about it. When it comes to PV input, Num. of MPP Trackers is 2. Max.PV array power is 6600W+6600W. Max. input current is 22/22Adc. Max.PV Isc is 37A/37Adc. Max.voltage of open circuit is 500Vdc. MPPT voltage range is 125-425Vdc. The following link is a diagram of PV input data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620100015263.jpg
1. What's the grid/generator input voltage range of FX-12K-SL inverter? 2. What's the frequency range when it comes to FX-12K-SL inverter's grid/generator input? 3. What's the max.AC bypass current when it comes to FX-12K-SL inverter? | This is FX-12K-SL inverter. Here's a datasheet about it. When it comes to Grid/Generator input, input voltage range is 90-280Vac. Frequency range is 50/60Hz. Max.AC bypass current is 63Aac. The following link is a diagram of Grid/Generator input data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620100321594.png
1. What's FX-12K-SL inverter's MPPT tracking efficiency? 2. What's max.efficiency of FX-12K-SL inverter? 3. What's European efficiency of FX-12K-SL inverter? | This is FX-12K-SL inverter. Here's a datasheet about it. MPPT tracking efficiency is 99.9%. Max. efficiency is 97.5%. European efficiency is 97%. The following link is a diagram of efficiency data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620100435362.png
1. Which kind of protection does FX-12K-SL inverter have? | This is FX-12K-SL inverter. Here's a datasheet about it. It has PV Input Lightning Protection, Anti-islanding Protection, PV String Input Reverse Polarity Protection, Insulation Resistor Detection, Residual Current Monitoring Unit, Output Over Current Protection, Output Shorted Protection. When it comes to Surge Protection, DC type II/AC type II. As to Over Voltage Category, DC type II/AC type III. The following link is a diagram of its protection data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620100720177.png
1. What's FX-12K-SL inverter's on-grid standard's certified specifications? 2. What's FX-12K-SL inverter's safety's certified specifications? 3. What's FX-12K-SL inverter's EMS's certified specifications? | This is FX-12K-SL inverter. Its On-grid standard's certified specifications is EN50549, NRS-097. Safety's certified specifications is IEC62109-1, IEC62109-2. EMS's certified specifications is EN61000-6-1, EN61000-6-3. It has RoHS certified specifications The following link is a diagram of its certified specifications data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620101501568.png
1. What's the operating temperature range of FX-12K-SL inverter? 2. What's FX-12K-SL inverter's noise? 3. What's the cooling method of FX-12K-SL inverter? 4. What's the communication port of FX-12K-SL inverter? | This is FX-12K-SL inverter. Here's some basic data about it. Its parallel capacity is 6. Operating temperature range is -25~60°C, >45°C derated. Humidity range is 0-100%. Warranty years is 5 years. Noise is <60dB. Protection Degree is IP65. Cooling Method is Heat sink + intelligent fan cooling. Self-consumption is <100W. Dimensions are 670*440*240mm. Weight is 37kg. Communication port is RS485 / CAN / USB / Dry contact. External Modules (Optional) is Wi-Fi / GPRS. The following link is a diagram of its basic data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250620101751059.png