## Sheet1
Question | Answer
1. What is the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter typically used for? 2. Can the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter support life-sustaining medical devices? 3. What grid types are compatible with the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 4. What components are needed for a complete hybrid solar system using the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. Is there a voltage limitation when using the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter in a TT grid system? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The hybrid solar system is usually composed of the PV array, hybrid inverter, lithium battery, loads and power grid. Below is the link to the schematic diagram of the hybrid system. https://hanchuess-file-eu.oss-eu-central-1.aliyuncs.com/Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612111756731.png (NOTICE:The system is not suitable for supplying life-sustaining medical devices. It cannot guarantee backup power in all circumstances.) The applicable grid types for the EnValt FX-25K/30K/36K/40K/50K/80K-T series are TN-S, TN-C,TN-C-S and TT. When applied to the TT grid, the voltage of N to PE suggests less than 30V. This is the link to the applicable grid types. https://hanchuess-file-eu.oss-eu-central-1.aliyuncs.com/Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612111756745.png
1. What is the primary function of the EnValt FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How does the FX-25K/30K/36K/40K/50K/80K-T storage inverter integrate PV, batteries, and the grid? 3. Can the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter manage both solar and battery power with the grid? 4. What components does the EnValt FX-25K/30K/36K/40K/50K/80K-T inverter connect to for power management? 5. Is the FX-25K/30K/36K/40K/50K/80K-T series inverter designed for intelligent energy dispatching between solar, battery, and grid? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The EnValt FX-25K/30K/36K/40K/50K/80K-T series inverter is also known as hybrid inverter or storage inverter, which is mainly used to combine the PV array, lithium battery, loads and power grid to realize intelligent power management and dispatching.
1. What are the available models in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Can you list all the models included in the FX-25K/30K/36K/40K/50K/80K-T series inverter? 3. What is the model range for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverters? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter includes 7 models which are listed below: CESS-HY-25K, CESS-HY-30K, CESS-HY-36K, CESS-HY-40K, CESS-HY-50K, CESS-HY-40K-P, CESS-HY-50K-P.
1. Where can I see the appearance and wiring layout of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Are there any diagrams showing the terminal connections for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. How are the wiring terminals arranged on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can you provide visual references for the physical design of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Where are the connection ports located on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png Wiring terminals are at the bottom of the inverter, as shown in the table below. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is Item 1 (Display and LED panel) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Where can I see the operating status on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What information does the display panel show on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How do I check the working status of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Where is the display located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? ） | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 1 is Display and LED panel, which displays the operation information and working states of the inverter. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the function of Item 2 (Hanger) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I properly mount my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter on the wall? 3. Where is the hanger located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can the hanger support the full weight of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What should I check before hanging my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter on the wall? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 2 is Hanger, which is used to hang the inverter on the wall-mounting bracket.. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the purpose of Item 3 (DC switch) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I safely turn off the DC power to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the DC switch located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. When should I use the DC switch on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Is the DC switch easily accessible on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter for emergency shutdowns? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 3 is DC switch, which is used to safely disconnect the DC circuit. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. How many PV connectors does Item 4 (DC input terminal) have on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What type of solar panels can I connect to the DC input terminals on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where exactly is the DC input terminal located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I connect all 8 pairs of PV connectors simultaneously on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Is there any difference in DC input terminals between FX-25K/30K/36K/40K/50K/80K-T and CESS-HY-40~50K-P models? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 4 is DC input terminal, which is PV connector(FX-25K/30K/36K/40K/50K/80K-T 8 pairs / CESS-HY-40~50K-P 6 pairs). 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the function of Item 5 (Battery input terminal) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I properly connect my battery to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the battery input terminal located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What type of battery connectors are compatible with my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Is there a specific procedure for connecting/disconnecting batteries to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 5 is Battery input terminal, which is battery connector. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the COM1 port used for on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I connect WiFi/LAN/4G modules to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the COM1 port located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I use both WiFi and 4G connections simultaneously on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What type of communication modules are compatible with the COM1 port on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 6 is COM1 port, which is WiFi/LAN/4G module connector. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What devices can be connected to the COM2 port on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I connect a meter or BMS to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the COM2 port located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I use the COM2 port for RS485 communication with my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What is the DRED/DO connector used for on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 7 is COM2 port , which is Meter/BMS/RS485/DRED/DO Connector. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What type of signals can the COM3 port handle on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I connect analog output devices to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the COM3 port located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I use the COM3 port for both digital and analog outputs on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What devices are typically connected to the 4-20mA AO port on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 8 is COM3 port, which is DO/0-10V AO/4-20mA AO Connector. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the purpose of Item 9 (On-grid output terminal) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I properly connect the grid power cables to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the on-grid output terminal located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What type of cables should I use for the on-grid connection on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Is there any safety precaution I should take when connecting to the on-grid output terminal of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 9 is On-grid output terminal, which is used for On-grid output cable connection. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is the function of Item 10 (Back-up output terminal) on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How do I connect emergency backup devices to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where is the backup output terminal located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What appliances can be safely powered through the backup output on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Are there any special wiring requirements for the backup output connection on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 10 is Back-up output terminal, which is used for Back-up output cable connection. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What is Item 11 (Generator input terminal) supposed to do on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Why can't I use the generator input on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter right now? 3. Where is the generator connector located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. When will the generator input function be available for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. How do I contact EnValt about activating the generator input on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The appearance of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. Iterm 11 is Generator input terminal, which is Generator connector (This function is temporarily unavailable. Please contact EnValt if necessary). 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612134156407.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612135901672.png
1. What does the display screen look like on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Can you show me the control panel of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. How do I check the settings on my FX-25K/30K/36K/40K/50K/80K-T series series hybrid inverter's display? 4. Is there a picture of the interface for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Where can I see the display layout for the EnValt FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The inverter display interface of the FX-25K/30K/36K/40K/50K/80K-T series inverter is shown in the link below. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png
1. Where is the power and alarm indicator located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Why isn't the power and alarm indicator light on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter lighting up? 3. What does it mean when the power and alarm indicator is off on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How can I tell if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is powered on? Which light should I check? 5. The right-side indicator light on my EnValt FX-25K/30K/36K/40K/50K/80K-T series hybrid inverterisn't lit, what's wrong? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Power and Alarm Indicator is located on the right side of the display. When its status is off, it indicates that the device has no power. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. What does it mean when the green light of power and alarm indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is blinking fast? 2. Why is the green light of power and alarm indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter pulsing slowly? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's green light of power and alarm indicator is breathing, what does this indicate? 4. What are the different green light patterns light of power and alarm indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter telling me? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series.The Power and Alarm Indicator is located on the right side of the display. When its status is Green, which has three situations: (1) Quick flashing: it indicates that the inverter entered self-test status. (2) Slow flashing: it indicates that the inverter entered waiting status. (3) Breathe flashing: it indicates that the inverter entered waiting status. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the orange light of power and alarm indicator breathing on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does a flashing orange light of power and alarm indicator mean on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's orange light of power and alarm indicator is pulsing, should I be worried? 4. How do I know when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's battery is getting too low? 5. What warning does a breathing orange light of power and alarm indicator give on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Power and Alarm Indicator is located on the right side of the display. When its status is Orange with breathe flashing, it indicates that the device has battery warning, the battery power is about to reach the SOC protection value. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the red light of power and alarm indicator constantly on for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What should I do when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's power and alarm indicator shows a solid red light? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's power and alarm indicator has a steady red indicator, does this mean there's a problem? 4. How do I check the error when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's red light of power and alarm indicator stays on? 5. The red alarm light of power and alarm indicator is lit on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what's wrong with it? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Power and Alarm Indicator is located on the right side of the display. When its status is Red and constantly lit, it indicates that the device has detected an alarm or fault. View the fault information on the display. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Where is the grid indicator located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does it mean when the grid light is off on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Why isn't the grid indicator lit up on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How can I tell if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter has lost grid connection? 5. The upper left indicator is off on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, is the grid down? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Grid Indicator is located at the upper left side of the display. When its status is off, it indicates that the grid lost. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the grid indicator flashing slowly on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does a slow flashing grid light mean on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's grid light is blinking slowly, is this normal? 4. How do I fix the slow flashing grid indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. The upper left light is blinking slowly on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what should I do? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Grid Indicator is located at the upper left side of the display. When its status is slow flashing, it indicates that the inverter detected grid but not running in on-grid mode. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the grid indicator constantly lit on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does it mean when the grid light stays on continuously for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Is it normal for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's grid indicator to be always on? 4. How do I know if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is operating in on-grid mode? 5. The upper left light is always lit on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what does this indicate? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Grid Indicator is located at the upper left side of the display. When its status is constantly lit, it indicates that the inverter works in on-grid mode. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the communication indicator constantly green on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does a solid green light mean for the communication indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Is it good that my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's communication light stays green? 4. Where can I find the communication status indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. The lower left light is solid green on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what does this tell me? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Communication Indicator is located at the lower left side of the display. When its status is Green and constantly lit, it indicates that the inverter communication is running normally. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the communication indicator flashing green on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does a blinking green light mean for the communication indicator on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's communication light is flashing green - is this normal? 4. How can I tell if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is communicating with EMS? 5. The lower left light is flashing green on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what's happening? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Communication Indicator is located at the lower left side of the display. When its status is Green and flashing, it indicates that the inverter communicates with EMS or Master inverter through RS485 or CAN. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the communication indicator solid orange on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what does it mean? 2. What should I check when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter shows a steady orange communication light? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's communication indicator stays orange, does this mean it's not working with the smart meter? 4. How do I troubleshoot the constant orange light on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's communication indicator? 5. The lower left light is solid orange on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, is the smart meter connection broken? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Communication Indicator is located at the lower left side of the display. When its status is Orange and constantly lit, it indicates that the inverter isn’t communicating with EnValt smart meter. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Why is the communication indicator solid red on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, what does this indicate? 2. What should I do when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter shows a steady red communication light? 3. My FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's communication indicator stays red, does this mean it's not talking to the battery? 4. How can I fix the connection issue when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter displays a constant red communication light? 5. The lower left light is solid red on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, is there a problem with the battery communication? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Communication Indicator is located at the lower left side of the display. When its status is Red and constantly lit, it indicates that the inverter isn’t communicating with the BMS. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. How do I wake up the display when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter screen goes dark? 2. Why won't my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter display turn on automatically? 3. What should I do if the screen on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is black? 4. Is there a way to turn on the display of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter when it's off? 5. The display on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter is not showing anything, how can I make it work again? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. When the display is off to save power, press the button to wake it up. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. How do I use the button on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter to change display information? 2. What's the difference between short press and long press on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's control button? 3. Where is the parameter setting button located on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can you explain how to operate the power/alarm indicator button on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What functions does the button near the power indicator control on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The Button upon Power and Alarm Indicator is used to switch display information and set parameters by short press or long press. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612140628608.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. Where can I find the meaning of symbols on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Is there a guide to understand all indicator symbols on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. How do I interpret the different symbols displayed on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What does each symbol represent on the control panel of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Can I get a reference chart for the status symbols on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is a table of symbols and their detailed descriptions on the inverter. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613110512098.png
1. What do the three indicator lights on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter mean? 2. Where can I find a diagram showing all the indicator lights and buttons on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. How do I read the different status lights on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can you show me where the display screen and control buttons are located on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Is there a visual guide to understand all the indicator lights on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. This inverter provides comprehensive information about three indicator lights (each with their respective status descriptions), along with specifications for the display screen and control buttons. The following link provides detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612162306452.png
1. How does Self-Consume Mode work on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What is the power supply priority in Self-Consume Mode for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Can I stop sending power to the grid in Self-Consume Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. When will my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter use battery power in Self-Consume Mode? 5. How does my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter decide when to use grid power in Self-Consume Mode? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of Self-Consume Mode: (1) In this working mode, when the power from the PV array is sufficient, PV power will supply the loads, battery, and grid in the order of loads first, battery second, and grid last. (You can set the power to the grid to 0W when the local grid doesn’t allow inverter power to feed to the grid). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612163813514.png (2) When the PV power is insufficient, the battery will discharge to supply loads, and the grid will join in if the battery is not enough to supply loads. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612163845597.png
1. How does Peak Load Shifting mode work on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What happens when my home's power usage exceeds Pmax in Peak Load Shifting mode on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Can I set the Pmax value myself for Peak Load Shifting on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. When will my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter use battery power in Peak Load Shifting mode? 5. Why won't my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter cover all excess power if load exceeds inverter capacity in Peak Load Shifting mode? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of Peak load Shifting (Load Shifting): (1) Set the maximum power Pmax (kVA) contracted with the grid. When the load consumption is less than the Pmax, the PV will charge the battery first, and the grid supplies the load. When the battery is full, PV will supply the load together with the grid, but the battery doesn't. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612164410310.png (2) When the load consumption exceeds the Pmax, the inverter will take power from the battery and PV to supply power to the load to compensate for the power that exceeds the Pmax. (NOTICE: To realize the “Peak load Shifting” function, the load power that exceeded Pmax has to be within the inverter max output power, otherwise, the inverter will only output the max power which allowed.) https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612164759139.png
1. When should I use Priority Grid Mode on my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. In Priority Grid Mode, what's the power supply order for my FX-25K/30K/36K/40K/50K/80K-T (solar vs. battery vs. grid)? 3. Can my FX-25K/30K/36K/40K/50K/80K-T charge batteries from the grid in this mode? 4. How does my FX-25K/30K/36K/40K/50K/80K-T handle insufficient solar power in Priority Grid Mode? 5. What happens to excess solar energy in Priority Grid Mode with my FX-25K/30K/36K/40K/50K/80K-T? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of Priority Grid Mode: (1) When the PV power is sufficient, it will be dispatched in the following sequence: loads first, the grid second, and the battery last.PV→Loads→Grid→Battery https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627094011020.png (2) When the PV power is insufficient, the PV and the battery will supply loads together. when the battery power is insufficient(or the battery reaches the End SOC), the grid will join together to supply loads.PV+Battery(+Grid)→Loads https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627094025139.png
1. How does Back-Up Mode work on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. When will my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter start using battery power in Back-Up Mode? 3. Does my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter keep charging the battery when grid is available in Back-Up Mode? 4. What powers my home during a blackout when using Back-Up Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. How do I know if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter has switched to backup power during an outage? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of Back-Up Mode: (1) In this working mode, the inverter will use the power from PV or grid to charge the battery until it is fully charged, and as long as the grid is there, the battery won’t discharge. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612165454014.png (2) When the grid fails, power from PV and battery will supply loads connected on the back-up side (UPS). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612165511583.png
1. How do I set up custom charging schedules in User-Defined Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Can I choose whether to use grid power for charging in User-Defined Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What happens when my solar production is insufficient during my preset time period in User-Defined Mode on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How does the battery discharge work during my scheduled periods in User-Defined Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Can I set different power levels for different times of day in User-Defined Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of User-Defined Mode: (1) In this working mode, you can set charge/discharge power and time in the App, inverter will use the power from PV or grid (whether to use can be set in the App) to charge the battery in the predetermined period. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612165853184.png (2) Inverter will use power from PV and battery to supply loads in the predetermined period and the insufficient part will be supplied by the grid. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612165920688.png
1. How does Off-grid Mode work on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What powers my home first in Off-grid Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. When will my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter use battery power in Off-grid Mode? 4. How does my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter handle excess solar power in Off-grid Mode? 5. What happens when solar power is insufficient in Off-grid Mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes and you can configure the operation mode as per your preference in the App. Below is the working process and operating principle of Off-grid Mode: (1) In the purely off-grid mode, power from PV will supply the back-up loads first and then charge the battery if there's surplus power. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612170127827.png (2) When the power from PV isn’t enough, the battery will discharge to supply back-up loads together with PV. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250612170146276.png
1. What are the five operation modes available on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How many operation modes available on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Where can I configure the operation modes for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I customize the operation settings for each mode on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. EnValt CESS-HY Hybrid inverter has six basic operation modes, they are Self-Consume Mode, Peak load Shifting (Load Shifting), Priority Grid Mode, Back-Up Mode, User-Defined Mode and Off-grid Mode. And you can configure the operation mode as per your preference in the App.
1. How fast does my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter switch to backup power during an outage? 2. What types of appliances should I avoid connecting to the backup output on my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Why won't my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter switch to backup mode sometimes? 4. Can I run my air conditioner on backup power with my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. How does cold weather affect the backup performance of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Normally, the Back-Up switching time is less than 20ms. However, some external factors may cause the system to fail on switching to Back-up Power Supply Mode. Therefore, the conditions for using the Back-Up function smoothly are as follows for your awareness. (1) Do not connect loads that are dependent on a stable energy supply for a reliable operation. (2) Do not connect the loads whose total capacity is greater than the maximum Back-Up capacity. (3) Do not connect the loads that may cause very high start-up current surges, such as non-frequency conversion air conditioning, vacuum cleaner or half-wave loads such as hair dryer, heat gun, hammer drill. (4) Due to the condition of the battery itself, battery current might be limited by some factors, including but not limited to the temperature and weather.
1. Why does my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter keep restarting? 2. How long will my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter take to restart after overload protection? 3. What should I do if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter keeps triggering overload protection? 4. Why does the restart time increase when my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter repeatedly goes into overload protection? 5. How can I prevent my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter from entering overload protection mode? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series.The inverter will restart in case of overload protection. The time required for restarting will increase (5 min at most) if overload protection repeats. Try to reduce Back-Up load power within maximum limitation or remove the loads which may cause very high start-up current surges.
1. How should I inspect my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter when it arrives to check for shipping damage? 2. What should I do if I find damage to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter right after delivery? 3. Who should I contact first if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter arrives damaged - EnValt or the shipping company? 4. What kind of photos do I need to provide when reporting damage to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Why is it important to inspect my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter immediately upon receiving it? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The device is thoroughly tested and strictly inspected before delivery. Nonetheless, damage may still occur during shipping. For this reason, please conduct a thorough inspection after receiving the device. Contact EnValt or the transport company in case of any damage or incompleteness, and provide photos to facilitate services.
1. What accessories should come with my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter when I receive it? 2. How can I verify if all included parts are present in my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter package? 3. Where can I find the complete packing list for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What should I do if some accessories are missing from my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter package? 5. Is there a reference guide showing all standard accessories included with the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is a packing list of the inverter. The package of the inverter includes the following accessories. Please check whether the accessories in the packing box are complete when receiving the goods. A:Inverter (1pcs) B:Inverter bracket (1pcs), Bolt assembly (4pcs), M6 screws (2pcs) C: AC connector set (3 pcs) D: PV terminal (FX-25K/30K/36K/40K/50K/80K-T 8 pairs ) E: Battery terminal (1 pairs) F: Meter with 3 CTs (1pcs) G: COM2 connector set (1pcs) H: COM3 connector set (1pcs) I: Monitoring device (1pcs) J: 10m meter communication cable (1pcs), 3m battery communication cable (1pcs) K: PE terminal(1pcs) L Quick Installation Guide The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613111614299.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613111633942.png 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613111654997.png
1. How should I properly store my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter when not in use? 2. What are the recommended temperature and humidity conditions for storing my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. Can I stack multiple FX-25K/30K/36K/40K/50K/80K-T series hybrid inverters during storage? 4. Why is it important to keep the original packaging for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What is the maximum safe stacking height for storing multiple FX-25K/30K/36K/40K/50K/80K-T series hybrid inverters? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below are some important notes for inverter storage: (1) Do not dispose of the original packing case. It is recommended to store the device in the original packing case when the device is decommissioned. (2) The storage temperature and humidity should be in the range of -30℃ and+ 60℃, and less than 90%, respectively. (3) If a batch of inverters needs to be stored, the height of each pile should be no more than 4 levels.
1. Where is the best place to install my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter indoors/outdoors? 2. How much weight can the wall support for installing my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What temperature range is safe for operating my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How high should I mount my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter for easy maintenance? 5. Can I install my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in direct sunlight? 6. What safety precautions should I take when installing my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter around children? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The EnValt FX-25K/30K/36K/40K/50K/80K-T series inverters are designed with IP65 protection enclosure for indoor and outdoor installations. When selecting an inverter installation location, the following factors should be considered: ① The wall on which the inverters mounted must be able to withstand the weight of the inverter. ② The inverter needs to be installed in a well-ventilated environment. ③ Do not expose the inverter directly to strong sunlight to prevent excessive temperature operation. The inverter should be installed in a place with shelter to prevent direct exposure to sunlight and rain. ④ Install the inverter at eye level for easy inspection of screen data and further maintenance. ⑤ The ambient temperature of the inverter installation location should be between -30℃ and 60℃. ⑥ The surface temperature of the inverter may reach up to 75℃. To avoid risk of burns, do not touch the inverter while it's operating and inverter must be installed out of reaching of children
1. Can my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter be installed outdoors? 2. What safety precautions should I consider when choosing an installation spot for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. How does the IP65 rating affect where I can install my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What factors should I consider for easy maintenance access to my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. Are there any restrictions on what can be placed near my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is a detail requirements for installation location of inverter: Select an optimal mounting location for safe operation, long service life and expected performance. ① The inverter with protection rating IP65 can be installed both indoors and outdoors. ② Install the inverter at a place convenient for electrical connection, operation, and maintenance. (Warning: Do not put flammable and explosive articles around the inverter.) Recommended installation location as shown in the following image. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613140348642.png
1. How much space needed for FX-25K/30K/36K/40K/50K/80K-T inverter? 2. What is minimum space under FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Where see FX-25K/30K/36K/40K/50K/80K-T inverter space picture? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For installation spacing, reserve enough clearance around the inverter to ensure sufficient space for heat dissipation. Recommended installation spacing is reserving ≥300mm clearance above, ≥450mm below, and ≥600mm on both sides as shown in the following image. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613140408733.png
1. How far apart should I install multiple FX-25K/30K/36K/40K/50K/80K-T hybrid inverters? 2. What is the minimum space needed between two FX-25K/30K/36K/40K/50K/80K-T inverters? 3. Where can I see the official spacing diagram for multiple FX-25K/30K/36K/40K/50K/80K-T hybrid inverters? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. In case of multiple inverters, reserve specific clearance between the inverters. Each inverter must maintain ≥600mm clearance on both left and right sides. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613142126695.png
1. How should I arrange multiple FX-25K/30K/36K/40K/50K/80K-T inverters in a small space? 2. What's the distance needed when installing FX-25K/30K/36K/40K/50K/80K-T inverters back-to-back? 3. Where can I see the back-to-back installation diagram for FX-25K/30K/36K/40K/50K/80K-T inverters? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. When installing inverters back-to-back, the distance between every two inverters should be at least 600 mm. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613142410837.png
1. How should I mount my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter - vertically or horizontally? 2. Can I install my FX-25K/30K/36K/40K/50K/80K-T inverter at an angle or upside down? 3. Where can I see the correct installation position for my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For installation angle, you should install the inverter vertically. Never install the inverter horizontally, or at forward/backward tilted, or upside down. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613142654419.png
1. What are the exact dimensions of the wall bracket for my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. Where can I see step-by-step pictures for installing my FX-25K/30K/36K/40K/50K/80K-T inverter bracket? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For bracket installation, dimensions of wall bracket (mm) are shown in the following image. The length of the bracket is 780mm, the width of the bracket is 45mm. There are four screw holes with a diameter of 12mm on the bracket, and the distance between two screw holes on a single side is 130mm. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613143823967.png Below is the detailed installation tutorial for bracket installation: ① Level the assembled inverter-bracket by using the level, and mark the positions fordrilling holes on the mounting bracket. Drill the holes by using a hammer drill. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613143916247.png ② Secure the inverter-bracket with bolts. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613143940962.png
1. How do I properly mount my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter on the bracket? 2. What type of screws should I use to secure my FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Is there a visual guide showing how to hang the FX-25K/30K/36K/40K/50K/80K-T inverter correctly? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For mounting the inverter, you should lift the inverter, hang the back rail on the fixed bracket carefully. Secure the inverter with M6 screws(two sides). The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613150529581.png
1. How do I properly ground my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. Which wire should I connect first when installing my FX-25K/30K/36K/40K/50K/80K-T inverter? 3. How should I ground multiple FX-25K/30K/36K/40K/50K/80K-T inverters together? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For external ground connection, you should connect the inverter and ground bar through PE wire to achieve the purpose of grounding protection. Please always remember wiring the PE wire before wiring other wires. (DANGER: Do not connect the N-wire as a protective ground wire to the inverter DANGER casing. Otherwise, it may cause electric shock.) (NOTICE: Reliable grounding is good for resisting surge voltage shock and improving EMI performance. Inverters must be well-grounded. For a system with only one inverter, just ground the PE cable. For a multi-inverter system, all inverters PE wire need to be connected to the same grounding copper bar to ensure equipotential bonding.)
1. Where is the grounding terminal located on my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. How do I connect the ground wire to my FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Can you show me where to connect the ground wire on my FX-25K/30K/36K/40K/50K/80K-T inverter? 4. Is there a picture showing the ground terminal connection for my FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is ground terminal connection steps: ① The external grounding terminal is located at the lower right side of the inverter. ② Fix the grounding terminal to the PE wire with a proper tool and lock the grounding terminal to the grounding hole in the lower right side of the inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613151415252.png
1. Where can I find the electrical connection guide for my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. Can I see the official electrical connection checklist for the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What safety steps should I follow when connecting wires to my FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is the detailed checklist for Electrical Connection: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613151844118.png
1. What does the wiring diagram show for my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. How should I wire my FX-25K/30K/36K/40K/50K/80K-T inverter to meet local electrical codes? 3. Where can I see the official wiring diagram for the FX-25K/30K/36K/40K/50K/80K-T series? 4. Does the FX-25K/30K/36K/40K/50K/80K-T inverter wiring differ by country/region? 5. What components are shown in the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter wiring diagram? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For electrical wiring , this diagram below shows EnValt FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter wiring structure and composition, concerning the real project, the installation and wiring have to be in line with the local standards. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613153608441.png
1. How should I wire a single FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. Can the neutral line be isolated when wiring my FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Where can I find the basic wiring diagram for my FX-25K/30K/36K/40K/50K/80K-T inverter? 4. Are there special wiring requirements for a single FX-25K/30K/36K/40K/50K/80K-T inverter installation? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For single inverter wiring, this diagram below is an example without special requirement on electrical wiring connection. Neutral line of AC supply can be isolated or switched. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613153825200.png
1. Where can I see the Australia-approved wiring diagram for the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. What are the specific grounding requirements for FX-25K/30K/36K/40K/50K/80K-T inverters in Australia/New Zealand under AS/NZS 3000? 3. How should grid and backup neutrals be connected for FX-25K/30K/36K/40K/50K/80K-T systems in New Zealand to ensure backup functionality? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. This diagram below is an example for Australia and New Zealand. Neutral line of AC supply must not be isolated or switched, and the neutral line of GRID side and BACK-UP side must be connected together according to the wiring rules AS/NZS_3000. Otherwise, BACK-UP function will not work. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613154134001.png
1. What safety check should I do before connecting AC wires to my FX-25K/30K/36K/40K/50K/80K-T inverter? 2. What power grid specifications work with the FX-25K/30K/36K/40K/50K/80K-T three-phase inverter? 3. Do I need separate breakers for my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter's grid and backup connections? 4. Can I connect appliances directly to my FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. Do I need utility approval before connecting my FX-25K/30K/36K/40K/50K/80K-T inverter to the grid? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For AC side requirements, there are four notcies: ① An independent AC breaker is required in both on-grid and back-up output side, and any loads cannot be connected with inverter directly. ② Before making the connection of AC cable, please confirm all DC & AC power source are disconnected from the inverter. ③ The EnValt FX-25K/30K/36K/40K/50K/80K-T series three-phase high voltage hybrid inverter applies to the three-phase power grid with a voltage of 230/400V and a frequency of 50/60Hz. ④ Connect the inverter to the grid only after getting an approval from the local electric power company.
1. What type of AC breaker is required for the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. How do I choose the right overcurrent protection device for my FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What cable sizes can I use with the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 4. What is the difference between flexible and hard cable requirements for the FX-25K/30K/36K/40K/50K/80K-T? 5. Where can I find the official cable specifications for the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. A three-phase AC breaker needs to be installed on the AC side of the FX-25K/30K/36K/40K/50K/80K-T. To ensure that the FX-25K/30K/36K/40K/50K/80K-T can safely disconnect itself from the power grid when an exception occurs, select a proper overcurrent protection device in compliance with local power distribution regulations and Max. input (output) current of FX-25K/30K/36K/40K/50K/80K-T AC side. The allowable AC cable of wire diameter and cross-sectional area for EnValt FX-25K/30K/36K/40K/50K/80K-T are as shown in the following: The diameter range of the cable is 20 - 30 millimeters. For flexible cables, the cross - sectional area is 10 - 25 square millimeters. For hard cables, the cross - sectional area is 10 - 35 square millimeters. (Notice: Determine whether an AC circuit breaker with greater overcurrent NOTICE capacity is required based on actual conditions.) https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613155733475.png
1. What is the recommended residual current for FX-25K/30K/36K/40K/50K/80K-T inverter? 2. What type of residual current monitoring device is integrated in the FX-25K/30K/36K/40K/50K/80K-T series inverter, and how does it function during a fault? 3. Does the FX-25K/30K/36K/40K/50K/80K-T series inverter require an external RCD, and which type is recommended? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For residual current monitoring device, it displays interfaceWith an integrated universal residual current monitoring device, the inverter will disconnectimmediately from the mains once a fault current with a value exceeding the limit isdetected. However if an external residual current device (RCD) (type A is recommended) is mandatory, the switch must be triggered at the residual current. RCD of other specifications can also be used according to local standard. (1) The recommended residual current of CESS - HY - 25K and CESS - HY - 30K is 300mA. (2) The recommended residual current of CESS - HY - 36K is 360mA. (3) The recommended residual current of CESS - HY - 40K and CESS - HY - 40K - P is 400mA. (4) The recommended residual current of CESS - HY - 50K and CESS - HY - 50K - P is 500mA. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613161009238.png
1. What precautions are mandatory before making electrical connections to the FX-25K/30K/36K/40K/50K/80K-T inverter? 2. At what stage should the AC circuit breaker be connected for the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What are the key safety dangers to avoid when installing the AC connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. When installing the AC connector, there are some dangers that should be avoided. (1) High voltage may be present in inverter! (2) Ensure all cables are voltage-free before electrical connection. (3) Do not connect the AC circuit breaker until all inverter electrical connections are completed.
1. Where is the AC terminal block located on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. What are the installation steps and torque requirement for tightening the nut on the FX-25K/30K/36K/40K/50K/80K-T inverter's AC connector? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The AC terminal block is on the bottom side of the inverter. Here is the steps of installing the AC connector. ① Seal accessory option.The recommended outer diameter of the cable is 20-24 mm and 24.5~30mm.If the outer diameter of the cable is greater than 24mm, remove part 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613162734538.png ② According to the figure 5-4, select an appropriate cable, peel the insulation sleeve of AC cable off for 95-100mm, and peel off the end of 3L /PE / N wires for 15mm. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613162753117.png ③ Thread the stripped wire into the lock nut and the main body in turn (the multi-core multi-strand copper wire cable needs to be riveted to the cord end terminal). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613162809735.png ④ Insert the cable into the rubber core according to the line sequence,observe the perspective hole, the cable is in place, and the torque of the crimping screwdriver is 5 ± 0.1N.m. (WARNING : The cord end terminals must be locked tightly, and make sure it won’t be loose after a long period of use.) https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613162823509.png ⑤ Insert the main body into the rubber core and hear the "click" sound, then tighten the nut with an open-ended wrench (torque 10.0±0.1N·m) and complete the installation with a "click, click, click". https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250613162842036.png
1. What are the proper steps to remove the AC connector from the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to remove the AC connector from the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below are the steps of removing the AC Connector: ① Hold the unlocking buckle with one hand and rotate it in the marked direction, and rotate the nut in the opposite direction with the other hand. ② Use a screwdriver to align the unlocking position, press and hold the main body and pull back to complete the removal. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616090632345.png (CAUTION: Please distinguish the on-grid and back-up port, and don’t mix up the on-grid port and back-up port when making the connection.)
1. What types of network connections does the INV-Logger A210 monitoring device support for the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. What happens when both WiFi and LAN connections are active simultaneously for the INV-Logger A210 monitoring device on the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Where can I find instructions for setting up WiFi connection for the INV-Logger A210 monitoring device with the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For monitoring device installation, INV-Logger A210(Monitoring device) supports both WiFi and LAN connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616091130900.png If you select WiFi connection, the operation method is described in "9.APP Guide". If you select LAN connection, see the following contents and steps. Tips: When WiFi and LAN are connected at the same time, the communication method will be prioritized to LAN.
1. What are the steps for installing the monitoring device on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How should the network cable be prepared and connected to the INV-Logger A210 on the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What are the size and shape requirements for the network cable used with the FX-25K/30K/36K/40K/50K/80K-T inverter's monitoring device? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below are the steps of monitoring device installation: Step1: Remove the "Plastic Nut" and "Sealing Ring" in turn. Step2: Pass the network cable plug through the"Plastic Nut" and "Sealing Ring” (with opening) in thedirection as shown in the figure 2-1. Step3: Fully embed the "Sealing Ring" into the"Plastic Nut". Step4: Connect the "RJ45 Plug" to the Ethernet Port(inside) and tighten the "Plastic Nut" for better waterproofing. Step5: Connect the "INV-Logger A210" to the "COM1" as shown in the figure 5-12. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616091718402.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616091735298.png Note: Due to limited space, only RJ45 plug without protective cap can be used. 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616091826494.png The network cable is required to be circular or oval, and the diameter of the networkcable needs to be greater more than 5.5mm and less than 6.5mm in order to be properly sealed.
1. How to remove the network cable of the FX-25K/30K/36K/40K/50K/80K-T series inverter | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. If you want to remove the network cable, unscrew the plastic case and seal-ing ring, and usea one-piece screwdriver to press in the way shown below, then pull out the cable. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616092148200.png
1. Where should the CT (Current Transformer) be installed for the FX-25K/30K/36K/40K/50K/80K-T series inverter's metering system? 2. What are the installation location requirements for the Smart Meter when used with the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Can the CT cable length be extended for the FX-25K/30K/36K/40K/50K/80K-T inverter's metering system? 4. How should the arrow direction on the CT be aligned when installing it with the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For Meter and CT Connection, the current Transformer, also called CT, is usually installed on the L wires between the house loads and the power grid. The Meter can be installed in the AC combiner box or other places that are unable to be touched by children. CT cable with length of 2m, it’s fixed and can’t be extended. The CTs have been connected to the Smart Meter when you received them, and you just need to follow the wiring diagram in the Meter to connect CT. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616092617066.png The directction of the arrow isconsistent with the direction ofthe arrow inside the CT. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616092754080.png (Notice: CT installation direction should strictly follow the instruction in the user manual, otherwise, the inverter may not be working normally. The CT has to be corresponding with the port in the meter, and the connection between CT and Meter needs to be reliable, otherwise, the CT measurement accuracy may be affected.) (Note:Please choose the appropriate CT size according to your needs.)
1. What is the function of terminals L1, L2, L3 and N on the FX-25K/30K/36K/40K/50K/80K-T series inverter's meter? 2. For the FX-25K/30K/36K/40K/50K/80K-T series inverter's meter, what is the purpose of terminals L1-S1, L1-S2, L2-S1, L2-S2, L3-S1 and L3-S2? 3. What is the function of the RS485-2 terminal in the FX-25K/30K/36K/40K/50K/80K-T series inverter's meter? 4. Which terminals in the FX-25K/30K/36K/40K/50K/80K-T series inverter's meter are reserved? 5. What is the function of the Type-C terminal in the FX-25K/30K/36K/40K/50K/80K-T series inverter's meter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Meter terminals definition as shown in table below: 1. In the first four rows of the table, NO.1-4 have definitions of L1, L2, L3 and N respectively, and their functions are "L1/L2/L3/N connect to grid to detect power grid voltage". 2. For NO.5-10 rows, the definitions are L1-S1, L1-S2, L2-S1, L2-S2, L3-S1 and L3-S2 respectively, and the function is "To detect the CT current and direction". 3. Then comes the RS485 part, where the function of RS485-2 is "Communicate with hybrid inverter", and the other RS485 is "Reserve". 4. Both ANT and LAN parts are "Reserve". 5. In the Type-C part, the definition is Type-C and the function is "Specified Debug Interface. Do not use it by non-professionals". https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616093510225.png
1. How can I know the definition and function of each pin of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. what are the definitions and functions of METER (RJ45-1) and BMS（RJ45-)1 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 3. what are the definition and function of Pin 3 and Pin 4 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. what are the definition and function of Pins 5-8 and 15-16 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 5. what are the definition and function of Pin 11 and Pin 12 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 6. what are the definition and function of Pin 13 and Pin 14 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 7. what are the definition and function of Pin 17 and Pin 18 of 5-12A COM2 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For the communication connection, all communication ports are in the multifunction communication Port at the bottom of inverter which including Meter port, CAN port, BMS port, EMS port, DRED port. DO port, 0-10V AO port, 4-20mA AO port. Here is the figure of 5-12A COM2 port. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616094051888.png Below is a pin definition and function table of 5-12A COM2 port: 1. METER (RJ45-1): Defined as RS485, and the function is to communicate with meter. 2. BMS (RJ45-1): Defined as CAN, and the function is to communicate with the Battery Management System (BMS). 3. Pins 1 and 2: Pin 1 is defined as COM, and Pin 2 is defined as NO (Normally Open), and the function is DO-1 (Multifunction Relay) and Load control (eg.SG ready heat pump). 4. Pins 3, 4, 19, 20: These pins are defined as empty (/), and the function is Reserved. 5. Pins 5-8 and 15-16: Pin 5 is defined as DRM4/8, Pin 6 is defined as DRM3/7, Pin 7 is defined as DRM2/6, Pin 8 is defined as DRM1/5, Pin 15 is defined as COM D/0, and Pin 16 is defined as REF D/0. The functions are marked as "DRED For Australia and New Zealand", "RCR For Germany and some other European countries" and "Grid/diesel generator Dl signal". 6. Pins 11 and 12: Pin 11 is defined as Emergency stop +, Pin 12 is defined as Emergency stop -, and the function is Emergency stop. 7. Pins 13 and 14: Pin 13 is 485 B1 and Pin 14 is 485 A1, with the function marked as EMS (Energy Management System). 8. Pins 17 and 18: Pin 17 is CANL_P and Pin 18 is CANH_P, and the function is for the parallel connection of inverters. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627101007558.png
1. How can I know the definition and function of each pin of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. what are the definition and function of Pins 1-6, 9-10, 13-16 of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 3. what are the definition and function of Pin 7 and Pin 8 of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. what are the definition and function of Pin 11 and Pin 12 of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 5. what are the definition and function of Pin 17 and Pin 18 of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 6. what are the definition and function of Pin 19 and Pin 20 of 5-12B COM3 port on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the figure of 5-12B COM3 port. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616101004224.png 1. Pins 1-6, 9-10, 13-16: These pins are defined as empty (/), and the function is Reserved. 2. Pins 7 and 8: Pin 7 is defined as COM, and Pin 8 is defined as NO, and the function is DO-2 (Multifunction Relay). 3. Pins 11 and 12: Pin 11 is defined as COM, and Pin 12 is defined as NC, and the function is DO-3 (Multifunction Relay). 3. Pins 17 and 18: Pin 17 is defined as 4-20mA_OUT, and Pin GND is defined as NC, and the function is 4-20mA analog output. 3. Pins 19 and 20: Pin 19 is defined as GND, and Pin 20 is defined as 0-10V_OUT, and the function is 0-10V analog output.
1. What's the steps of assembling the multi-com connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to assemble the multi-com connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the steps of assembling the multi-com connector: ① Unscrew the swivel nut from the connector. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616103418922.png ② Take out the terminal block. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616103442356.png ③ Remove the seal and lead the cable through the cable gland. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616103507245.png
1. What's the steps of connecting the Meter and BMS communication cables on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to connect the Meter and BMS communication cables on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the steps of connecting the Meter and BMS communication cables: (NOTE: The communication between meter/BMS and inverter is RJ45 interface cable.) ① Thread the RJ45 plug of appropriate length through the swivel nut, and insert it into the open side of the rubber gasket. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104053092.png ② Insert one side of the RJ45 plug into the RJ45 port of terminal block. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104114001.png ③ Insert another side of the communication cable into the meter RS485 port or BMS CAN port.
1. What's the steps of connecting other cables on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to connect other cables on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the steps of connecting other cables: ① Thread the cable of appropriate length through the swivel nut and the housing. Remove the cable jacket and strip the wire insulation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104137024.png ② (Optional) When using a multi-core multi-strand copper wire cable, connect the AC wire head to the cord end terminal (hand-tight). In case of single-strand copper wire, skip this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104733526.png ③ Fix all the wires to the terminal plug according to the assignment and tighten to a torque of 1.2+/-0.1N·m with a screwdriver. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104756563.png ④ Pull the wires outward to check whether they are firmly installed.Insert the terminal block into the connector until it snaps into place with an audible click. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104807708.png ⑤ Fasten the swivel nut. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616104821529.png
1. What's the steps of installing the COM Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to install the COM Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the steps of installing the COM Connector: ① Remove the waterproof lid from the COM terminal. ② Insert the COM connector into COM terminal on the bottom of the inverter until there is an audible click. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616105040810.png
1. How can I verify if my selected battery is compatible with the FX-25K/30K/36K/40K/50K/80K-T series inverter before purchase? 2. What should I do if my battery isn't listed in EnValt's approved battery list for the CESS-HY-30K energy storage system? 3. Where can I find the official battery approval list for the CESS-HY-40K inverter to ensure proper system operation? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Before purchasing the battery, you need to make sure the battery you selected is in the battery approval list of EnValt, otherwise, the system may not work properly. Please contact your installer or EnValt service team for confirmation if you’re not sure about it.
1. Where can I get the figure of 5-24 RJ45 terminal connection sequence and definition on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. what is the definition of each terminal connection sequence on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is a figure of 5-24 RJ45 terminal connection sequence and definition: 1. No.1's color is Orange & White, which has no Meter Side and Battery Side is RS485_A3. 2. No.2's color is Orange , which has no Meter Side and Battery Side is RS485_B3. 3. No.3's color is Green & White, which has no Battery Side and Meter Side is RS485_B2. 4. No.4's color is Blue, which has no Battery Side and Meter Side is CANH_B. 5. No.5's color is Blue & White, which has no Battery Side and Meter Side is CANL_B. 6. No.6's color is Green, which has no Battery Side and Meter Side is RS485_A2. 7. No.7's color is Brown & White, which has no Battery Side and Meter Side is RS485_B2. 8. No.8's color is Brown , which has no Battery Side and Meter Side is RS485_A2. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616105803828.png
1. What type of communication cable is required for EMS control of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. How does the EMS communicate with the FX-25K/30K/36K/40K/50K/80K-T series inverter? 3. What interface is used for EMS and inverter communication in the FX-25K/30K/36K/40K/50K/80K-T series? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. An EMS communication cable needs to be connected when to control the operation of a hybrid inverter through the EMS, and communication between EMS and inverter is RS485.
1. How does the FX-25K/30K/36K/40K/50K/80K-T inverter handle DI control for DRM(DRED), RCR, and ATS signals? 2. Can the FX-25K/30K/36K/40K/50K/80K-T inverter connect to DRED, RCR, and ATS simultaneously? 3. What are the pin configurations for DRM(DRED), RCR, and ATS on the FX-25K/30K/36K/40K/50K/80K-T inverter's COM2 port? 4. Which pins on the FX-25K/30K/36K/40K/50K/80K-T inverter's COM2 support both DRM(DRED) and RCR signals? 5. Where can I find the detailed DI port wiring diagram for the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About DI control, Inverter supports DRM(DRED), RCR and ATS signal input via DIport. When the inverter is connected to DRED, RCR and ATS carnnot be connected. RCR and ATS can connect to the inverter simultaneously. 1. COM2 Pin 5: DRM4/8 with DRM(DRED) and RCR. 2. COM2 Pin 6: DRM3/7 with DRM(DRED) and RCR. 3. COM2 Pin 7: DRM2/6 with DRM(DRED) and RCR. 4. COM2 Pin 8: DRM1/5 with DRM(DRED) and RCR. 5. COM2 Pin 15: COM D/0 with DRM(DRED) and ATS. 6. COM2 Pin 16: REF D/0 with DRM(DRED), RCR and ATS. The following link provides detailed information: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627095814746.png
1. What is DRED in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Where can I get DRED wiring diagram of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What function of each DRED mode in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For DRED, DRM and Ripple Control support only one function at the same time. DRED (Demand Response Enabling Device) interface is special reserved for Australia and New Zealand according to their safety regulation, and EnValt doesn’t provide the DRED device for the customer. The inverter supports the demand response modes as specified in the standard AS/NZS 4777. The inverter has integrated a terminal block for connecting to a DRED. DRED wiring diagram (hybrid inverter) as below: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616110703494.png DRED mode as shown in table below: 1. DRM 0: Operate the disconnection device. 2. DRM 1: Do not consume power. 3. DRM 2: Do not consume at more than 50% of rated power. 4. DRM 3: Do not consume at more than 75% of rated power and source reactive power if capable. 5. DRM 4: Increase power consumption (subject to constraints from other active DRMs). 6. DRM 5: Do not generate power. 7. DRM 6: Do not generate at more than 50% of rated power. 8. DRM 7: Do not generate at more than 75% of rated power and sink reactive power if capable. 9. DRM 8: Increase power generation (subject to constraints from other active DRMs. 10. Priority: DRM1 > DRM2 > DRM3 > DRM4, DRM5 > DRM6 > DRM7 > DRM8. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616111447072.png (NOTE: There is a resistor between15(COM D/0) and 16(REF D/0), do not move the resistor while wiring.)
1. What is RCD in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Where can I get RCD wiring diagram of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What function of each RCD switch mode in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What is the priority of RCD in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. RCR (Ripple Control Receiver) interface is special reserved for Germany and some other European country according to their safety regulation, and EnValt doesn’t provide the RCR device for the customer. In Germany and some European areas, a ripple control receiver is used to convert a power grid dispatching signal to a dry contact signal. The dry contact is required for receiving the power grid dispatching signal. RCR wiring diagram (hybrid inverter) as below: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616111533680.png RCR operation mode as shown in table below: 1. When switch mode (External RCR device) is K1 turn on, feed-in output power (in % of the Rated AC output powe) is 100%. 2. When switch mode (External RCR device) is K2 turn on, feed-in output power (in % of the Rated AC output powe) is 60%. 3. When switch mode (External RCR device) is K3 turn on, feed-in output power (in % of the Rated AC output powe) is 30%. 4. When switch mode (External RCR device) is K4 turn on, feed-in output power (in % of the Rated AC output powe) is 0%. 5. RCR priority: K1<K2<K3<K4 The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616111910351.png
1. What is the function of the multifunction dry contact relay in the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 2. What are the maximum voltage and current specifications for the DO dry contact port on the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. How does the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter support SG-Ready heat pump control? 4. Which SG-Ready modes (Mode 2 and Mode 3) are supported by the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter for heat pump integration? 5. Where can I find detailed wiring diagrams for SG-Ready heat pump control with the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For multifunction relay, the inverter is equipped with a multifunction dry contact relay, which helps turn the loads on or off when an extra contactor is connected, or startup the diesel generator when the diesel generator startup signal is connected. (NOTICE: Maximum voltage and current at DO dry contact port:30VDC 1A.) (NOTE: For more installation and setup information, please contact EnValt) Below is SG Ready heat pump control: https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627130919381.png Hybrid Inverter is matched with a SG-ready heat pump with dry contact port, which can realize heat pump integrated energy system management. Most heat pumps today have a digital control input, such as SSG ready, allowing external signals to influence the working of the heat pump. Please refer tto the heat pump manufacturer's manual for more information on the specific control input of the heat pump. https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627131208843.png 1. Mode 1, the "State" is "OFF". "SG ready recommendation" indicates "HP switched off". The "Validity" is marked as "/", and "DO - 1 state" is also "/". 2. Mode 2, the "State" is "Normal". "SG ready recommendation" says "HP operates in normal energy efficient mode". The "Validity" is "Yes", and "DO - 1 state" is "0". 3. Mode 3, the "State" is "Recommended ON". "SG ready recommendation" states "HP is operating in an enhanced heating mode". The "Validity" is "Yes", and "DO - 1 state" is "1". 4. Mode 4, the "State" is "Forced ON". "SG ready recommendation" shows "HP has to switch on". The "Validity" is marked as "/", and "DO - 1 state" is "/". (NOTICE: Hybrid Inverter only supports Mode 2 and Mode 3 of SG ready. Inverter switches between mode 2 and mode 3.)
1. What is the function of the "Disable" work mode in the load management of the CESS - HY - 25~50K hybrid inverter? 2. When should the "Feed - in Power Control" mode within the Smart Mode of the CESS - HY - 25~50K inverter be used? 3. How does the "Smart Mode - Battery SOC Control" of the CESS - HY - 25~50K inverter operate? 4. What is the significance of the "Smart Mode - Time Control" in the load management of the CESS - HY - 25~50K hybrid inverter? 5. Can I manually control the heat pump or smart load in the CESS - HY - 25~50K inverter, and if so, how? 6. Give me a diagram of work modes to control smart loads in the CESS - HY - 25~50K hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About load management, Hybrid Inverter has three work modes to control smart loads (such as SG ready heat pump). 1. The work mode is "Disable". Its application description is that "Disable" means not using the load management function. 2. The work mode is part of "Smart Mode" - "Feed-in Power Control". The application description is to set the feed - in power threshold for triggering the heat pump entering Mode3 or turning on the smart load. When the meter detects the feed - in power equal to or greater than the set value, the inverter relay will close and the heat pump will enter the heating mode or smart loads start working. This control mode is suggested to use in the system without power export limitation. 3. The work mode is "Smart Mode - Battery SOC Control". The application description is to set the battery SOC threshold for triggering the heat pump entering Mode3 or turning on the smart load. When the inverter detects the battery SOC value equal to or greater than the set value, the inverter relay will close and the heat pump will enter the heating mode or smart loads start working. This control mode is suggested to use in the system with power export limitation. 4. The work mode is "Smart Mode - Time Control". The application description is to set the operation periods for heat pump mode three or smart load according to user habits or preferences. Up to 3 periods can be set. When this mode is enabled, it has a higher priority than other modes within the period. Outside the period, the heat pump or smart load operates according to the parameters set by the smart mode. If this mode is not enabled or no period is set, it operates according to the parameters set by the smart mode throughout the day. 5. The work mode is "Manual Mode". Its application description is to manually control the heat pump entering Mode3 or start the smart load. More configuration items for heat pumps or other smart loads areavailable on the APP or platform. The following link provides detailed information: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250627131533520.png
1. Can the general version of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter support parallel connection for backup power applications? 2. Is it possible to connect a single PV string to multiple FX-25K/30K/36K/40K/50K/80K-T inverters in a parallel system? 3. Can one meter or the same CT be shared between multiple FX-25K/30K/36K/40K/50K/80K-T inverters in a parallel setup? 4. Is it allowed to connect one battery bank to multiple FX-25K/30K/36K/40K/50K/80K-T inverters in a parallel configuration? 5. Can the on-grid and backup side of the FX-25K/30K/36K/40K/50K/80K-T inverter be directly connected to a generator in a parallel system? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For parallel system, there are six warning: 1. For the general version, back-up cannot connect in parallel. For advanced applications, please contact our after-sales department. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130516032.png 2. Single PV string cannot connect to multiple inverters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130529169.png 3. One meter cannot be connected to multiple inverters. Different CTs cannot connect to the same line cable. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130548700.png 4. One battery bank cannot be connected to multiple inverters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130604314.png 5. The on-grid and back-up side cannot be connected to and generator directly.For advanced applications, please contact our after-sales department. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130618216.png 6. The back-up side cannot be connected ongrid side or grid. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616130633121.png (NOTICE: For more installation and setup information about parallel system, please contact EnValt.)
1. Does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter come with a built-in emergency stop function? 2. How do I connect an external emergency stop switch to the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. Is the emergency stop switch included in the accessory box of the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 4. Where can I find the wiring diagram for connecting the emergency stop function on the FX-25K/30K/36K/40K/50K/80K-T inverter? 5. What type of external switch is required to activate the emergency stop function on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For emergency stop, EnValt FX-25K/30K/36K/40K/50K/80K-T hybrid inverter comes standard with Emergency stop function, and you can use this function by connecting an external switch into the Emergency stop interface if it requires in the installation place. The external switch doesn't include in our accessory box. Below is the emergency stop connection diagram: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616131039420.png
1. What safety precautions should be taken when performing electrical operations on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Can different models of PV modules be connected to the same string in the FX-25K/30K/36K/40K/50K/80K-T inverter system? 3. What is the maximum PV input voltage allowed for the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. When should the DC switch and AC circuit breaker be connected during installation of the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. What voltage warning should technicians be aware of when working with the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Danger: High voltage may be present in the inverter!Ensure all cables are voltage-free before performing electrical operations.Do not connect the DC switch and AC circuit breaker before finishing electrical connection. NOTICE: For best practice, ensure PV modules of the same model and specifications are connected in each string. WARNING: PV Max. Input voltage is 850V, otherwise inverter will be waiting.
1. What certification standards must the external DC switch meet for the FX-25K/30K/36K/40K/50K/80K-T series inverter in Australia and New Zealand markets? 2. What is the minimum current rating requirement for DC switches used with the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 3. Where can I find the recommended electrical connection diagram for the DC switch installation with the FX-25K/30K/36K/40K/50K/80K-T inverter? 4. What safety margin should be considered when selecting a DC switch for the PV array connected to the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For PV side requirements, system layout of units with external DC switch: ① Local standards or codes may require PV systems that fit with an external DC switch on the DC side. The DC switch must be able to safely disconnect the open-circuit voltage of the PV array plus a safety reserve of 20%. Install a DC switch to each PV string to isolate the DC side of the inverter. ② The DC switch has to be certified by AS 60947.3:2018 and AS/NZS IEC 60947.1:2020 in Australia and New Zealand market. The Max. current of the DC switch matching with FX-25K/30K/36K/40K/50K/80K-T inverter is no less than 40A. We recommend the following electrical connection. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616131621878.png
1. What are the photovoltaic cable specifications required for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What is the recommended conductor core section size for PV cables connected to the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What is the proper cable stripping length for PV cable installation with the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. What is the acceptable outside diameter range for photovoltaic cables used with the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. What size of PV cable should be selected for proper connection to the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. You should select the appropriate photovoltaic cable, for cable requirements, outside diameter is 5.9-8.8 mm and conductor core section is 4 mm². And cable stripping length is 7mm.
1. What's the steps of assembling the PV Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to assemble the PV Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For assembling the PV Connector, there are five steps: WARNING: Before assembling the DC connector, make sure that the cable polarity is correct. ① Peel off the DC cable insulation sleeve for 7 mm. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132556018.png ② Disassemble the connector in the accessory bag. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132611535.png ③ Insert the DC cable through the DC connector nut into the metal terminal and press the terminal with a professional crimping plier (pull back the cable with some power to check if the terminal is well connected to the cable). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132626877.png ④ Insert the positive and negative cables into the corresponding positive and negative connectors, pull back the DC cable to ensure that the terminal is tightly attached in the connector. ⑤ Use an open-end wrench to screw the nut to the end to ensure that the terminal is well sealed. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132645823.png
1. What's the steps of installing the PV Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 2. How to install the PV Connector on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For installing the PV Connector, there are four steps: ① Rotate the DC switch to “OFF” position. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132916821.png ② Check the cable connection of the PV string for polarity correctness and ensure that the open circuit voltage in any case does not exceed the inverter input limit of 1,000V, PV Max. Input voltage is 850V, otherwise inverter will be waiting. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616132951373.png ③ Insert the positive and negative connectors into the inverter DC input terminals respectively, a click sound should be heard if the terminals are well connected. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616133013283.png ④ Seal the unused PV terminals with the terminal caps.
1. What safety precautions should be taken before connecting batteries to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For power cable of the battery connection, the following principles must be considered when making battery connection: ① Disconnect the AC breaker on the grid side. ② Disconnect the breaker on the battery side. ③ Turn the inverter DC switch to the “OFF” position. ④ Make sure the maximum input voltage of battery is within the inverter limitation. (NOTE:Please contact your battery supplier for detailed battery installation information.)
1. What are the DC cable specifications required for battery connection to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What is the required conductor core section size for battery cables used with the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What is the proper cable stripping length for battery cable installation on the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. What is the acceptable outside diameter range for battery DC cables connected to the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. What size of DC cable should be selected for proper battery connection to the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For power cable of the battery connection, you should select an appropriate DC cable. For cable requirements, outside diameter is 9.8±0.2 mm and Conductor core section is 25 mm². And cable stripping length is 20mm. (CAUTION: If the conductor core of the battery cable is too small, which may cause poor contact between the terminal and the cable, please use the cable specified in the above table, or contact EnValt to purchase terminals of other specifications.)
1. What is the proper insulation sleeve stripping length for battery cable connection to the FX-25K/30K/36K/40K/50K/80K-T inverter? 2. What is the correct assembly sequence for battery cable components when connecting to the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. How should I verify proper terminal connection when crimping battery cables for the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. What safety checks should be performed before connecting battery cables to the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. How can I confirm proper installation of battery connectors into the FX-25K/30K/36K/40K/50K/80K-T inverter terminals? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The following are precautions for power cable of the battery connection: ① Peel off the battery cable insulation sleeve for 20 mm. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616134243853.png ② Disassemble the connector in the accessory bag, Thread the cable into end cap, grommet, and cable gland in turn. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616134258513.png ③ Insert the battery cable through into the metal terminal and press the terminal with a professional crimping plier (pull back the cable with some power to check if the terminal is well connected to the cable). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616134313319.png ④ After the crimping is completed, push the cable gland, grommet and end cap at the plug end into place, and tighten the end cover with the thread of the plug unit. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616134325218.png (WARNING:① Before making the battery connector, please make sure the polarity of the cable is correct. ② Use a multimeter to measure the voltage of the battery pack and make sure the voltage is within the inverter limitation and the polarity is correct.) ⑤ Insert the positive and negative connector into the inverter battery terminals respectively, and a “click” sound represents the assembly in place. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616134342108.png
1. What should I do before starting the FX-25K/30K/36K/40K/50K/80K-T inverter for the first time? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. You should Check the following items before starting the inverter: ① All equipment has been reliably installed. ② DC switch and AC circuit breaker are in the "OFF" position. ③ The ground cable is properly and reliably connected. ④ The AC cable is properly and reliably connected. ⑤ The DC cable is properly and reliably connected. ⑥ The communication cable is properly and reliably connected. ⑦ The vacant terminals are sealed. ⑧ No foreign items, such as tools, are left on the top of the machine or in the junction box (if there is). ⑨ The AC circuit breaker is selected in accordance with the requirements of this manual and local standards. ⑩ All warning signs & labels are intact and legible.
1. What should I do to start up the FX-25K/30K/36K/40K/50K/80K-T inverter for the first time? 2. What should I do if the FX-25K/30K/36K/40K/50K/80K-T inverter does not work properly? 3. What should I do to calibrate the SOC during system use on the FX-25K/30K/36K/40K/50K/80K-T inverter? 4. What's the function of CESS-HY hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For commissioning procedure, if all of the items mentioned above meet the requirements, proceed as follows to start up the inverter for the first time. ① Turn on the AC breaker. ② Turn on the lithium battery switch. Power on the battery pack manually if a battery is equipped. ③ Turn on the DC switch, the DC switch may be integrated in the inverter or installed by the customer. ④ The inverter will work properly after turning on the DC and AC breakers on the condition the weather and grid meet requirements. The time for entering the operating mode may vary according to the chosen safety code. ⑤ Observe the LED indicator to ensure that the inverter operates normally. ⑥ After the inverter is started, please refer to the [Quick Installation Guide] which is attached to the access to configure the inverter. (NOTE1: If the inverter does not work properly, check the country code and battery ID Settings.① Select the safety code suitable for the country (region) where the inverter is installed at.② Select the battery ID suitable for the battery is installed.) (NOTE2: CT AUTO TEST FUNCTION CESS-HY hybrid inverter has the function of detecting the installation direction and phase sequence of CT. The system is installed, this function can be enabled on the APP for detection.) (NOTICE: SOC RESET FUNCTION When the inverter is turned on for the first time, the battery will be automatically charged to calibrate the battery SOC. After the battery is charged, this function will be turned off automatically (If you confirm that it is not necessary, you can manually turn off the function. We recommend to enable this function.)If you need to calibrate the SOC during system use, you can manually enable the function to calibrate the battery SOC on app or inverter screen. After the battery is fully charged, the function is automatically disabled again.)
1. What should I do when turning off the FX-25K/30K/36K/40K/50K/80K-T inverter? 2. What are the steps when turning off the FX-25K/30K/36K/40K/50K/80K-T inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. When turning off the inverter, please follow the steps below: ① Shut down the inverter through the APP or the button on the display first. ② Disconnect the breakers on the grid and load side. ③ Turn off the battery switch, and disconnect the DC breaker on the battery side (if any). ④ Wait 30 seconds and then turn the inverter DC switch to the “OFF” position. At this time, there is remaining power in the inverter capacitor. Wait for 10 minutes until the inverter is completely de-energized before operating. ⑤ Disconnect the AC and DC cables.
1. What type of display interface does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter use for operation monitoring? 2. How do I modify numerical parameters on the OLED display of the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. What is the proper way to confirm and save settings changes on the FX-25K/30K/36K/40K/50K/80K-T series inverter's display? 4. How long does the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter take to automatically save settings changes made through the OLED display? 5. What operational information can be viewed through the OLED display on the FX-25K/30K/36K/40K/50K/80K-T series inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. When the inverter is turned on, the following interfaces will be displayed on the OLED display, and the OLED display allows the user to check various operation information and to modify the settings of the inverter. (NOTE: If the parameter is a number short press to change the number, long press to confirm the number and jump to the next number. Please wait for 10 seconds and the inverter will automatically save your settings or modifications.)
1. What are the six possible working statuses displayed on the OLED screen of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Where can I see the visual representation of the main OLED display interface for the FX-25K/30K/36K/40K/50K/80K-T inverter? 3. How many different operational modes does the OLED display show for the FX-25K/30K/36K/40K/50K/80K-T series inverter? 4. What types of status information can be viewed on the OLED display of the FX-25K/30K/36K/40K/50K/80K-T hybrid inverter? 5. Does the OLED display of the FX-25K/30K/36K/40K/50K/80K-T inverter show both normal operation and fault status information? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the main window of OLED display: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616141303771.png There are six inverter working status: Waiting/Checking/On-Grid/Off-Grid/Fault Info/FW Updating.
1. What are the abbreviation and complete name in FX-25K/30K/36K/40K/50K/80K-T inverter OLED display? 2. What does "V-Ipv1/2"/"Ppv1/2"/"BAT"/"Charg."/"Dischg."/"V_L1: / V_L2: / V_L3"/"VbakL1: / VbakL2: / VbakL3"/"I_L1: / I_L2: / I_L3"/ "IbakL1: / IbakL2: / IbakL3"/"FreqL1: / FreqL2: / FreqL3"/"FW Updating" mean in FX-25K/30K/36K/40K/50K/80K-T inverter OLED display? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Below is the inverter display abbreviation and complete name reference table in OLED display: 1. V-Ipv1/2: PV input voltage and current of each MPPT 2. Ppv1/2: PV input power of each MPPT 3. BAT: Parameter Battery Parameter 4. Charg.: Charge 5. Dischg.: Discharge 6. V_L1: / V_L2: / V_L3: Three-phase AC voltage (On-Grid status) 7. VbakL1: / VbakL2: / VbakL3: Three-phase AC voltage (Off-Grid status) 8. I_L1: / I_L2: / I_L3: Inverter output current (On-Grid status) 9. IbakL1: / IbakL2: / IbakL3: Inverter output current (Off-Grid status) 10. FreqL1: / FreqL2: / FreqL3: Inverter output Frequency (Off-Grid status) 11. FW: Updating Firmware Updating The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616163605475.png
1. What are the abbreviation and complete name in FX-25K/30K/36K/40K/50K/80K-T inverter general setting? 2. What does "System Info"/"FM Version"/"DNS Addr"/"Modbus Addr" mean in FX-25K/30K/36K/40K/50K/80K-T inverter general setting? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the general setting figure of the FX-25K/30K/36K/40K/50K/80K-T series. (https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616143506598.png Below is the inverter's general setting abbreviation and complete name reference table: 1. System Info: System information 2. FM Version: Firmware version 3. DNS Addr: If DHCP is turned off, set the domain name server address 4. Modbus Addr: Modbus address The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616163639870.png
1. What are the abbreviation and complete name in FX-25K/30K/36K/40K/50K/80K-T inverter advance setting? 2. What does "Safety Set"/"Battery_ID Set"/"Work Moder"/"Export Limit" /"Feed in Grid"/"Reactive Modes"/"PF"/"Qt"/"Cosφ(P)"/"Q(U)'/"Fixed Q"/"On-Off Grid SW"/"Relax OffGrid"/"Offgrid ReConn."/"Load Shifting"/"SetMaxGrid"/"OnGrid SocProt."/"OnGrid EndSOC"/"OffGrid SocProt."/"OffGrid EndSOC"/"Unbalan. Output"/"System Maint."/"Multi-INV Role"/"SOC Reset"/"MPPT Parallel"/"MaxOutputSet"/"Export Control"/"N-PE Check"/"DI Ctrl "/"DRM"/"RCR"/"Emergency Stop"/"NO"/"NC"/"CommsWatchDog" mean in FX-25K/30K/36K/40K/50K/80K-T inverter advance setting? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the advanced setting of the FX-25K/30K/36K/40K/50K/80K-T series. The following links provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616144243237.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616144309081.png Below is the inverter's advanced setting abbreviation and complete name reference table: 1. Safety Set: Select the code that meet local regulatory requirements 2. Battery_ID: Set Select the battery model 3. Work Mode: Current work mode / work mode setting 4. Export Limit: On-grid export limit function switch 5. Feed in Grid: Set the percentage of the power that is allowed to feed to the grid 6. Reactive Modes: Reactive Power Mode 7. PF: "Under ""Reactive Mode" "The reactive power can be regulated by the parameter PF (Power Factor)." 8. Qt: "Under ""Reactive Mode" "The reactive power can be regulated by the parameter Q-Var limits (in %)." 9. Cosφ(P): "Under ""Reactive Mode""The PF changes with the output power of the inverter." 10 Q(U): "Under ""Reactive Mode""The reactive power changes with the grid voltage" 11. Fixed Q: The reactive power ratio when the "Reactive Mode" is Qt. 12. On-Off Grid SW: Off-grid function switch (If turn it on, the inverter will automatically switch to off-grid mode to ensure the back-up side power supply when the gird is abnormal or off, otherwise, there is no output on the back-up side) 13. Relax OffGrid: Reduce the switching sensitivity of the On/Off-grid (applied to the places where the grid is unstable or inverter always entered off-grid mode for some reasons) 14. Offgrid ReConn: When inverter is operating without grid, it will stop backup output after overload protection, and restart within the set time. 15. Load Shifting: Peakload shifting function switch 16. SetMaxGrid: Set max allowed power from grid (under the condition of Peakload Shifting is on) 17. OnGrid SocProt: On-grid battery SOC (State of Charge) Protection 18. OnGrid EndSOC: End-of-discharge SOC of on-grid 19. OffGrid SocProt: Off-grid SOC Protection 20. OffGrid EndSOC: End-of-discharge SOC of off-grid 21. Unbalan. Output: 3-Phase Unbalanced Output Switch when inverter work on On-grid state 22. System Maint: System maintenance, includes inverter stop and run, system restart 23. Multi-INV Role: In the multi-inverter parallel system, set the role of one inverter as the master and the other inverter as the slave. 24 SOC Reset: If turned it on, the battery will be automatically charged to calibrate the battery SOC. After the battery is charged, this function will be turned off automatically 25 MPPT Parallel: If MPPT is connected in parallel, enable this function. 26 MaxOutputSet: Select the maximum AC output power. Rated, Max. output power = Rated output power on the datasheet. Overload, Max. output power = Max. output power on the datashee. Limit, Max. output power <Rated output power on the datasheet 27 Export Control: In the power export limit on mode, when the communication between the inverter and meter or the inverter and datalogger is interrupted, select the inverter operation mode from one of the follows: Hard, inverter stops. Soft, inverter generates power as the "Feed in Grid" value set on the screen 28 N - PE Check: The N and PE shorting function on the BACK - UP side in the off - grid operation status. 29 DI Ctrl: DI Ctrl enable "DRM" or "RCR" function 30 DRM: Demand Response Modes 31 RCR: Ripple Control Receiver 32 Emergency Stop: Emergency stop switch device 33 NO: Normally open: Emergency Switch Normally Open, when switch closed, inverter stop. 34 NC: Normally closed: Emergency Switch Normally Closed, when switch open, inverter stop. 35 CommsWatchDog: When the function is turned on, the inverter stops working when communication with the master is lost. The following linka provide detailed information. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616163820662.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616164204137.png
1. Where can I access the "Country code (Safety code)" setting on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Here is the Country Code (Safety Code) Setting: Please set "Country code (Safety code)" under the menu "Safety Set" in " Advanced Settings ".Refer to “7.3 Advanced Setting” for more information.
1. How can I enable the Auto-Test function on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter show on the screen when the Auto-Test is successful? 3. What does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter show on the screen when the Auto-Test fails? 4. How do I check the Auto-Test results on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For Auto-Test, This function is disabled by default, and will be only functional in the safety code of Italy. Short press the button several times until "Auto Test CEI 0-21" displays on the screen, press and hold the button 3 seconds to activate “Auto Test". After the auto test is finished, short press the button several times until the screen displays "Auto Test Record", and hold the button 3 seconds to check the test results. The auto test will start when the correct test item is selected, and the test result will be displayed on the screen when it finished. If the test was successful, it will display "Test Pass", otherwise will display "Test Fail”. After each item tested, the inverter will reconnect to the grid and automatically start the next test according to the requirements of CEI 0-21.
1. How do I enable the Auto-Test function on the FX-25K/30K/36K/40K/50K/80K-T series inverter, and what are the specific steps? 2. Why is the Auto-Test function disabled by default in the FX-25K/30K/36K/40K/50K/80K-T series inverter, and where is it required to be used? 3. What does the FX-25K/30K/36K/40K/50K/80K-T series inverter display after completing the Auto-Test, and how can I check the results? 4. What happens if the Auto-Test fails on the FX-25K/30K/36K/40K/50K/80K-T series inverter, and does it automatically proceed to the next test? 5. How does the FX-25K/30K/36K/40K/50K/80K-T series inverter handle grid reconnection during the Auto-Test process according to CEI 0-21 standards? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. Connect the AC cable, auto test will start after the inverter connected to the grid, see the operation steps below: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616151253263.png
1. How do I enable or change the reactive power regulation mode on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, and is configuration software required? 2. In which markets is the reactive power regulation function enabled by default for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What are the different reactive power regulation modes available on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter, and how do they function? 4. How can I adjust the default setpoints for reactive power regulation on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What should I do if I need technical support for configuring reactive power settings on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 6. What does "Off"/"PF"/"Qt"/"Cosφ(P)"/"Q(U)" mode mean in FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. The inverter provides a reactive power regulation function. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616151718667.png This mode can be enabled via configuration software. It is enabled by default in some regions, such as AU, DE market. For information on how to change default setpoints please contact EnValt Technical Support at service@hanchuess.com. Descriptions of reactive power regulation mode: 1. Off: The PF is fixed at +1.000. 2. PF The reactive power can be regulated by the parameter PF (Power Factor). 3. Qt The reactive power can be regulated by the parameter fixed Q(in Pn%). 4. Cosφ(P) The PF changes with the output power of the inverter. 5. Q(U) The reactive power changes with the grid voltage. The following link provides detailed information. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616164247613.png
1. Is the reactive power regulation function disabled in 'Off' mode for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter？ 2. What is the power factor (PF) limit value of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in shutdown state? 3. Does the 'Off' mode of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter disable reactive power regulation? 4. Are there any other PF limit ranges in 'Off' mode for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For “Off” Modes, the reactive power regulation function is disabled. The PF is limited to +1.000.
1. What is the power factor (PF) range for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in PF mode? 2. How does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter calculate reactive power setpoint in PF mode? 3. In PF mode, does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter have a fixed power factor? 4. What does it mean when the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter operates at 0.8 leading power factor? 5. Can the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter inject reactive power into the grid when set to lagging PF mode? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For “PF” Mode, the power factor is fixed and reactive power setpoint is calculated according to the current power: The PF ranges from 0.8 leading to 0.8 lagging. Leading: the inverter is sourcing reactive power to the grid. Lagging: the inverter is injecting reactive power into the grid.
1. What is the reactive power ratio setting range for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in Qt mode? 2. How does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter regulate reactive power in Qt mode? 3. What is the relationship between reactive power ratio and reactive power regulation in the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter's Qt mode? 4. Does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter maintain fixed rated reactive power when operating in Qt mode? 5. How does the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter handle inductive versus capacitive reactive power regulation in Qt mode? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For “Qt” Mode, in the Qt mode, system rated reactive power is fixed, and the system injects reactive power according to the delivered reactive power ratio. The setting range of the reactive power ratio is -60%~60%, corresponding to the ranges of inductive and capacitive reactive power regulation respectively.
1. What is the range of the output power at P1 (Point A) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What is the range of the output power at P2 (Point B) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What is the range of the output power at P3 (Point C) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. What is the range of the power factor at K1 (Point A) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 5. What is the range of the power factor at K2 (Point B) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 6. What is the range of the power factor at K3 (Point C) on the Cosφ(P) mode curve for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 7. What is the voltage percentage range for Cosφ(P) function activation (Cosφ(P)_Enter - Voltage) on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 8. What is the voltage percentage range for Cosφ(P) function deactivation (Cosφ(P)_Exit - Voltage) on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For “Cosφ(P)” Mode, the PF of the inverter output varies in response to the output power of the inverter. “Cosφ(P)” Mode Parameter Descriptions as below: 1. "Cosφ(P)_P1 (Point A) is the output power at P1 on the Cosφ(P) mode curve (in percentage), with a range of 10% ~ 100%." 2. "Cosφ(P)_P2 (Point B) is the output power at P2 on the Cosφ(P) mode curve (in percentage), and the range is 20% ~ 100%." 3. "Cosφ(P)_P3 (Point C) is the output power at P3 on the Cosφ(P) mode curve (in percentage), having a range of 20% ~ 100%." 4. "Cosφ(P)_K1 (Point A) is the power factor at P1 on the Cosφ(P) mode curve, with a range of 0.8 ~ 1." 5. "Cosφ(P)_K2 (Point B) is the power factor at P2 on the Cosφ(P) mode curve, with a range of 0.8 ~ 1." 6. "Cosφ(P)_K3 (Point C) is the power factor at P3 on the Cosφ(P) mode curve, with a range of 0.8 ~ 1." 7. "Cosφ(P)_Enter-Voltage is the voltage percentage for Cosφ(P) function activation, and the range is 100% ~ 110%." 8. "Cosφ(P)_Exit-Voltage is the voltage percentage for Cosφ(P) function deactivation, with a range of 90% ~ 100%." https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616164330122.png Below is the Cosφ(P) Curve: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616153106003.png
1. What are the range values for all the parameters in the “Q(U)” mode (QU_V1, QU_Q1, QU_V2, QU_Q2, QU_V3, QU_Q3, QU_V4, QU_Q4, QU_Enter - Power, QU_Exit - Power) on the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. Where can I get Q(U) Curve of the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. For “Q(U)” Mode, the reactive power output of the inverter will vary in response to the grid voltage. “Q(U)” Mode Parameter Descriptions: 1. QU_V1: Grid voltage limit at P1 on the Q(U) mode curve, range is 80% ~ 100%. 2. QU_Q1: Value of Q/Sn at P1 on the Q(U) mode curve, range is 0 ~ 60%. 3. QU_V2: Grid voltage limit at P2 on the Q(U) mode curve, range is 80% ~ 100%. 4. QU_Q2: Value of Q/Sn at P2 on the Q(U) mode curve, range is -60% ~ 60%. 5. QU_V3: Grid voltage limit at P3 on the Q(U) mode curve, range is 100% ~ 120%. 6. QU_Q3: Value of Q/Sn at P3 on the Q(U) mode curve, range is -60% ~ 60%. 7. QU_V4: Grid voltage limit at P4 on the Q(U) mode curve, range is 100% ~ 120%. 8. QU_Q4: Value of Q/Sn at P4 on the Q(U) mode curve, range is 0 ~ -60%. 9. QU_Enter - Power: Active power for Q(U) function activation, range is 20% ~ 100%. 10. QU_Exit - Power: Active power for Q(U) function deactivation, range is 1% ~ 20%. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616164400205.png Below is the Q(U) Curve: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616153301024.png
1. How can I download the EnValt App for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2 Where can I find the QR code to download the EnValt App for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter？ 3. Is there a specific website for downloading the EnValt App related to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Can I download the EnValt App from mobile application stores for the FX-25K/30K/36K/40K/50K/80K-T series series hybrid inverter? 5. If I want to download the EnValt App for the FX-25K/30K/36K/40K/50K/80K-T series series hybrid inverter, are there multiple options available? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About app download, you can scan the QR code or visit the website to download the EnValt App: https://iess.hanchuess.com. You can also download the EnValt App from the App store or Google play. The QR-Code is shown below: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616154901137.png
1. How do I register an account for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 2. What steps are required to log in to the FX-25K/30K/36K/40K/50K/80K-T series hybrid invertersystem after registration? 3. How do I bind devices after logging in to the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. Where can I find the verification code during the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter registration process? 5. What information do I need to provide to complete the registration for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About registering and login of device, if you have already registered, you can log in directly . Then you can turn to "9.2.2 Bind decives". If you don't have an account yet, tap"Sign up" to register as shown in Fig. 1. In order to provide you with the basic functionality of our products / services, you are required to authorise your consent to the "Privacy Policy" and "Terms & Conditions". We promise to keep users' information strictly confidential and will not disclose users' private information to outside parties unless authorised by the user or required by law. Fill in the account informationAfter filling in the information for registration, tap "Get Verification Code" as shown in Fig. 2. We will send the verification code to your email.Fill in the code, and click on "Confirm" to log in, as shown in Fig. 3. Fig. 1 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616155516714.png Fig. 2 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616155535999.png Fig. 3 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616155601745.png
1. How do I add a new device to my existing station for the FX-25K/30K/36K/40K/50K/80K-T series series hybrid inverter? 2. What is the process for creating a new station with the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 3. What information do I need to provide when setting up a new station for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? 4. How do I configure the Wi-Fi network for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter during device binding? 5. Why can’t I find my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter during Bluetooth binding, and how do I fix it? 6. What should I do after successfully binding my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverterto the network? 7. How do I select and configure a specific FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter after binding multiple devices? 8. Can I remotely control my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverterafter setup, and how? 9. Where can I view the operational data of my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter besides the mobile app? 10. What should I do if I need advanced configuration settings for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About binding devices, You can jump to the relevant section referring to what you want to do: • Now you have a station, but need to setting the network for devices or add new devices to your station? - Please tap the "Add Device" button , as shown in Fig. 4. Then you can directly turn to b.Network configuration. • Now you don't have a station yet? -Tap "Add station" on the page, as shown in Fig. 5. a. Fill in the new station information You will need to fill in some information for the station, as shown in Fig. 6. • Address (optional): Your detailed address, we will only use it for after-sales service. • Electricity price setting (optional): After filled, you will be able to view the income and expenditure of your devices. Fig. 4 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161035900.png Fig. 5 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161054373.png Fig. 6 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161107946.png b. Network configuration Select the home Wi-Fi network you want to connect to (not 5GWiFi) and enter your WiFi password, as shown in Fig. 7. c. Bluetooth search Turn on your phone's Bluetooth, then select the devices you want to bind. Tap "Add" to add the devices to your station, as shown in Fig. 8. The SN on this page is the same as the SN on the logger. ! Tips: Please be sure to turn on the Bluetooth of the mobile phone, otherwise the binding function will not be available. Fig. 7 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161325513.png Fig. 8 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161341507.png Fig. 9 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161409074.png d. Binding completed After the devices are connected to the network and bound successfully, you will see the page shown in Fig. 9. Please tap "Next ". e. Choose the inverter: Choose one inverter to Setting. f. Local Setting: Then enter the local Setting page, as shown in Fig. 10. Click "Complete" to complete the Setting Fig. 10 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161627927.png Fig. 11 https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250616161640694.png ! Tips: • If you want to set more inverter configuration items, please contact your installer. • If you want to set up the inverter remotely, enter the "Home" page, select the device you want to control, and click "Control" to operate the device remotely. As the following fig. 11. Congratulations! You have done the basic setting. Now you can view your device data on APP. You can also view your device data by logging into https://iess.hanchuess.com, the website login password is the same as the APP account password.
1. How do I check my account information for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in the app? 2. What should I do if my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter has a malfunction or technical issue? 3. Where can I find the device manual for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in the app? 4. How do I access after-sales service options for my FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter in the app? 5. What is the customer support email for the FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter if I need assistance? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About account and service information, Tap "PERSONAL" to view account information and app settings. • Have any device malfunction or have technical problems? Tap "After Sales", and you will see how to contact the service. • Have any questions or suggestions about the APP? You can leave us a message in the "Suggestions feedback" or contact us at service@envalt-tech.com. We will deal with it for you as soon as we know. • How do I view the device manual in the app? Click "Data Center" on the "SERVICE" page to view the corresponding device information.
1. Give me a diagram of single FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter with diesel generator system. 2. What are the operation steps of single FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter with diesel generator system? 3. What should I notice with the single FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter with diesel generator system? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About single inverter with diesel generator system, below are notices and operation steps. The link below provides detailed infomations of system diagram: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630091819217.png Notices: ① This solution is suitable for single inverter and is not suitable for parallel systems. Dieselpowered is directly connected to the inverter Gen port. ② Diesel generator need to support the start&stop via the controls the start&stop of the DG via inverter COM3-7/8pin DO2 port. ③ Users can access manual bypass switch. In the event of an inverter failure, close the switch manually to power back-up loads. ④ Do not close the manual bypass switch and the on-grid&back-up side breaker at the same time. Disconnect the on-grid&back-up side circuit breaker before closing the manual bypass switch. Close the on-grid&back-up side circuit breaker and disconnect the manual bypass switch first. Operation steps: ① Referring to the diagram above, complete the wiring. ② Create a power station and add equipment through the APP. ③ Enter the <Inverter Detail> interface. Click <Remote control>. Click < Diesel Gen Setup >. Select <GEN port > in <Diesel Generator Connection Mode > menu. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630091912372.png ④ Enter< Diesel Gen Setup > interface to set <Diesel Generator Control Mode> and other parameters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630091939282.png
1. Give me a diagram of on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter. 2. What are the operation steps of on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter.? 3. What should I notice with on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter.? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About on-grid side parallel system, below are notices and operation steps. The link below provides detailed infomations of system diagram: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630092652677.png Notice: ① Up to 10 inverters on-grid side parallel is supported; The 25-50K series inverter can only be paralleled with the same model (the same rated power), and cannot be paralleled with different model(different rated power). ② It is recommended that PV and battery capacity connected with each inverter must be the same or close. ③ Parallel system is master and slave parallel. User need to set one of the inverters as the master and the other inverters as slaves through the screen or monitoring platform. ④ The master needs to communicate with the meter via RS485. Master and slave inverters communicate with each other via CAN. The communication port is COM2-pin17&18 (CANL_P&CANH_P). ⑤ Each inverter needs to be connected to a communication module. ⑥ In the parallel system, circuit breakers need to be installed on the on-grid/back-up AC output side and on-grid/back-up load side of the inverter. ⑦ In the parallel system, the DIP switch of the parallel CAN termination resistor of the first and last inverters needs to be turned to "ON". Operation step: ① Referring to the diagram above, complete the wiring. ② Create a power station and add all inverters into power station through the APP. ③ Designate an inverter as the master. Enter the <Inverter Detail> interface of the master. Click <Remote control>. Click <Function Setup >. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630092915743.png ④ Select <Parallel-Master > under <Multi Inverter Role > menu. Set the number of parallel units by <Number of parallel units> (range: 1~10). Set parallel address to 0 by<Parallel address> https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630092942119.png ⑤ The rest of the inverters are slaves. Select <Parallel-Slave> under < Multi Inverter Role > menu. Set the number of parallel units by <Number of parallel units> (range: 1~10). Set the slave address (range:1~9) in <Parallel address> . Starting from 1 in order (1, 2, 3... ) settings, do not skip the number setting, and do not set duplicate addresses. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630092959749.png
1. Give me a diagram of on&off-grid side parallel with diesel generator system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter. 2. What are the operation steps of on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter.? 3. What should I notice with on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter.? 4. What are the scenarios in the on-grid side parallel system of FX-25K/30K/36K/40K/50K/80K-T series hybrid inverter.? | This is an inverter of the FX-25K/30K/36K/40K/50K/80K-T series. About on&off-grid side parallel with diesel generator system, below are scenarios, notices and operation steps. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630095306525.png Scenario 1: Utility grid&DG both available; connect DG via ATS Scenario 2: Only DG available;DG connects grid port of backup box Scenario 3: Only utility grid available. Notice: ① Up to 4 inverters on-grid side parallel is supported; The 25-50K series inverter can only be paralleled with the same model (the same rated power), and cannot be paralleled with different model(different rated power). ② It is recommended that PV and battery capacity connected with each inverter must be the same or close. ③ Parallel system is master and slave parallel. User need to set one of the inverters as the master and the other inverters as slaves through the screen or monitoring platform. ④ The master needs to communicate with the meter via RS485. Master and slave inverters communicate with each other via CAN. The communication port is COM2-pin17&18 (CANL_P&CANH_P). ⑤ Each inverter needs to be connected to a communication module. ⑥ In the parallel system, circuit breakers need to be installed on the on-grid/back-up AC output side and on-grid/back-up load side of the inverter. ⑦ In the parallel system, the DIP switch of the parallel CAN termination resistor of the first and last inverters needs to be turned to "ON". ⑧ Diesel generator need to support the start&stop via the dry contact signal. DG communicates with the inverter through the inverter COM3-7/8pin DO2 port. The Grid Comm inverter controls the start&stop of the DG ⑨ On&off-grid parallel requires access to the backup box. Backup box communicates with the inverter via the master COM3-11/12pin DO3 port. Please refer to the manual for the model selection and installation guidance of the backup box. ⑩ The external ATS shall have a normally open (NO) output signal circuit of backup power supply (diesel generator) auxiliary contact, which communicates with the inverter through the master COM2-15/16pin DI port. Operation step: ① Referring to the diagram above, complete the wiring. ② Create a power station and add all inverters into power station through the APP. ③ The configuration mode of master and slave is the same as that of the grid-connected side. Please refer to the "On-grid side parallel" section above. ④ Set the diesel generator access mode: Scenario 1: Enter the <Inverter detail> page. Click <Remote control>. Click < the Diesel Gen Setup>. Select <ATS connection > under <Diesel Generator Connection Mode> menu .Please notice that set value of < Number of parallel units>should not exceed 4. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630094853656.png Scenario 2: Select <Grid port > under <Diesel Generator Connection Mode> menu. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630094922352.png Scenario 3: No setup is required. ⑤ Enter< Diesel Gen Setup > interface to set <Diesel Generator Control Mode> and other parameters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/CESS-HY-25~50K/20250630095018535.png