## Sheet1
问题 | 答案
1. What should I do if the delivery checklist for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is incomplete? 2. Who should I contact if the inverter or its accessories are damaged upon delivery of the FX-5K/6K/8K/10K/12K/15K/20K-T system? 3. What items are included in the delivery checklist for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. If the distributor cannot resolve delivery issues for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, are there alternative support channels? | This is an FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the delivery checklist (description and quantity) included with the package. Note: If the checklist is incomplete or any items are damaged, please contact your distributor. The following link is a schematic diagram of the delivery checklist. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616154411427.png
1. What should I do if the delivery checklist for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is incomplete? 2. Who should I contact if the inverter or its accessories are damaged upon delivery of the FX-5K/6K/8K/10K/12K/15K/20K-T system? 3. What items are included in the delivery checklist for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. How can I verify that the hardware descriptions and quantities on the delivery checklist match the actual contents for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. If the distributor cannot resolve delivery issues for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, are there alternative support channels? | This is an FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the delivery checklist (description and quantity) included with the package. Note: If the checklist is incomplete or any items are damaged, please contact your distributor. The following link is a corresponding description list of the delivery checklist. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616154517966.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616154517975.png
1. What are the specific packaging requirements for storing the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the permissible storage temperature range for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What are the humidity requirements for the storage environment of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? Is condensation allowed? 4. If the FX-5K/6K/8K/10K/12K/15K/20K-T inverter has been stored for more than 6 months, what special procedures are required before use? 5. Why must the FX-5K/6K/8K/10K/12K/15K/20K-T inverter undergo professional inspection after long-term storage before being put into operation? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product storage guidelines specify that it must be kept in its original packaging, which should not be tilted or inverted. The storage environment must maintain a temperature range of -30°C to +70°C and a relative humidity of 0% to 100% without condensation. Additionally, if the product has been stored for six months or longer, it must undergo a comprehensive inspection and testing by qualified personnel before being put into operation.
1. What are the exterior features of each side of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Where is the handle located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the position of the display area on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Detailed exterior description of the front, both sides, and bottom of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 5. Are there any differences between the actual appearance of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter and the images provided? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the appearance descriptions of its front, both sides, and bottom, along with corresponding description lists. Note: The provided images are for reference only, and the actual product received may vary. The following link is a schematic diagram of inverter appearance. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616160746229.png
1. What are the exterior features of each side of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Where is the handle located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the position of the display area on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Detailed exterior description of the front, both sides, and bottom of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 5. Are there any differences between the actual appearance of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter and the images provided? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the appearance descriptions of its front, both sides, and bottom, along with corresponding description lists. Note: The provided images are for reference only, and the actual product received may vary. The following link is a corresponding description list of inverter appearance. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616160746234.png
1. What are the exact length, width, and height dimensions of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the mounting hole spacing of the rear bracket for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What does the 3D design diagram of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter look like? 4. Does the installation of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter require additional clearance space? 5. What unit of measurement is used for the dimensional specifications of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the 3D design introduction, including dimensional specifications for the front view, top view, and side view, as well as the dimensions of the rear mounting bracket for inverter installation. Note: All dimensions are in millimeters (mm). The following link is a schematic diagram of 3D design introduction. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250616161342781.png
1. Where exactly is the SOLAR indicator positioned on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? Could you provide a schematic diagram for reference? 2. When the SOLAR indicator shows a steady white light on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, does this confirm normal photovoltaic power generation operation? 3. How will the SOLAR indicator display on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during cloudy days or low-light conditions? 4. What operational status does a steady white light on the SOLAR indicator represent in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. How will the SOLAR indicator appear when solar energy is being properly utilized by the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The SOLAR indicator is located at the top of the display panel. A glowing white light indicates that the inverter is operating normally and solar energy is available for use. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What causes the white flashing of the SOLAR indicator on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. How does the SOLAR indicator behave when the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is performing automatic self-checking? 3. Where is the SOLAR indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What will be displayed on the interface when the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is updating its firmware? 5. How to determine whether it's self-checking or firmware update when the SOLAR indicator flashes white on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The SOLAR indicator is positioned at the top of the display panel. A flashing white light indicates that the inverter is performing automatic self-checking or that firmware is being updated. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. How to determine whether the off SOLAR indicator on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter indicates device malfunction or genuine absence of solar energy input? 2. Why is the SOLAR indicator not lighting on my FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Does an off SOLAR indicator on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter signify a malfunction in the solar panels? 4. Where is the SOLAR indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Is it normal for the SOLAR indicator to remain off during cloudy conditions or insufficient sunlight on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The SOLAR indicator is positioned at the top of the display panel. An off indicator signifies that solar energy is unavailable. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. In the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, does a steadily illuminated BAT indicator confirm normal battery power availability? 2. What does a glowing white light on the BAT indicator signify in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What should be the normal status of the BAT indicator during battery power mode in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What are the indicators of normal operational status for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Where is the BAT indicator positioned on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The BAT indicator is located on the second row of the display panel. A glowing white light indicates normal inverter operation with battery energy available for use. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. How to distinguish between self-checking, firmware update, or low battery SOC when the BAT indicator flashes white in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What indication does the BAT indicator provide when the battery SOC is too low in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the status of the BAT indicator when self-checking or firmware update is incomplete in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What are the possible causes of a white flashing BAT indicator in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Where is the BAT indicator located on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The BAT indicator is located on the second row of the display panel. A flashing white light indicates that the inverter is performing automatic self-checking, or the firmware is being updated, or the battery SOC is low. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Will the FX-5K/6K/8K/10K/12K/15K/20K-T inverter completely stop battery charging/discharging functions when the BAT indicator is unlit? 2. Could prolonged unlit status of the BAT indicator potentially cause battery damage in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Why is the BAT indicator completely unlit on my FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What indicator behavior will be displayed when battery energy is unavailable in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Where is the BAT indicator positioned on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The BAT indicator is located on the second row of the display panel. An off indicator signifies that battery energy is unavailable. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What does a steady yellow ERR indicator indicate in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Where is the ERR indicator located on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Will system communication be affected when the ERR indicator shows a steady yellow light in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What ERR indicator behavior occurs during INV-Logger communication failure in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Will the ERR indicator remain steadily lit yellow after communication is restored in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The ERR indicator is located on the third row of the display panel. A glowing yellow light indicates communication failure with the INV-Logger A200. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. How to quickly view corresponding warning messages and event numbers when the ERR indicator flashes yellow in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What changes occur to the ERR indicator when warning messages appear in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How can I check relevant event information when warning faults occur in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What causes the ERR indicator to flash yellow in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Where is the ERR indicator located on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The ERR indicator is located on the third row of the display panel. A flashing yellow light indicates a warning fault, and the corresponding warning message and event number will be displayed on the inverter's user interface. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What causes the ERR indicator to flash red in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Where is the ERR indicator positioned on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Where can the error message be viewed when a fault triggers a steady red ERR indicator in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. How to troubleshoot when the ERR indicator remains steadily red but no error message appears on the user interface of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What changes occur to the ERR indicator when the system detects an error in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The ERR indicator is located on the third row of the display panel. A glowing red light indicates an error fault, and the corresponding error message and event number will be displayed on the inverter's user interface. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What does an unlit ERR indicator signify in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. How to verify normal operation of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter through the ERR indicator? 3. What should be the status of the ERR indicator during normal operation of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Where is the ERR indicator positioned on the display panel of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The ERR indicator is located on the third row of the display panel. An off indicator signifies normal inverter operation. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the EPS indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What does a steady white EPS indicator light indicate in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How does the EPS indicator appear when the FX-5K/6K/8K/10K/12K/15K/20K-T inverter operates in backup mode? 4. What is the status of the EPS indicator when the EPS port operates with load in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The EPS indicator is positioned on the left side of the fourth row of the display panel. A glowing white light indicates that the inverter's EPS port is operating with the load or running in backup mode. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the EPS indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What does a flashing white EPS indicator light indicate in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How to verify whether the EPS port is truly without connected load in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The EPS indicator is located on the left side of the fourth row of the display panel. A flashing white light indicates that the inverter's EPS port is operating without load but remains energized - do not touch the port. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the EPS indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the possible fault reasons when the EPS indicator shows a steady red light in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the status of the EPS indicator when the EPS port malfunctions in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The EPS indicator is located on the left side of the fourth row of the display panel. A glowing red light indicates a fault in the inverter's EPS port. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the EPS indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Under what conditions will the EPS indicator flash red in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the status of the EPS indicator when the EPS port is overloaded in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What actions should be taken when the EPS indicator flashes red in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The EPS indicator is positioned on the left side of the fourth row of the display panel. A flashing red light indicates that the inverter's EPS port is operating under overload conditions. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the EPS indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What does an off EPS indicator indicate in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the status of the EPS indicator when the EPS port is not operating in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The EPS indicator is located on the left side of the fourth row of the display panel. An off indicator signifies that the inverter's EPS port is not in operation. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. How to determine if the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is connected to the grid? 2. Where is the GRID indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter operate when the GRID indicator shows a steady white light? 4. What operational status does a glowing white GRID indicator represent in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The GRID indicator is located on the right side of the fourth row of the display panel. A glowing white light indicates the inverter is connected to the grid and feeding solar energy into the public power network. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the GRID indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What operating mode does a flashing white GRID indicator represent in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the grid connection status of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter when the GRID indicator flashes white? 4. Which GRID indicator status indicates the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is operating in off-grid mode? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T nverter. Below are the LED indicator specifications: The GRID indicator is located on the right side of the fourth row of the display panel. A flashing white light indicates the inverter is disconnected from the grid and operating in off-grid mode. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the GRID indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the grid connection status of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter when the GRID indicator shows a glowing red light? 3. How to determine if the FX-5K/6K/8K/10K/12K/15K/20K-T inverter has disconnected from the grid due to a fault? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The GRID indicator is located on the right side of the fourth row of the display panel. A glowing red light indicates the inverter has disconnected from the grid due to a fault. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. Where is the GRID indicator located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What operational status does an off GRID indicator indicate in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How to determine if the FX-5K/6K/8K/10K/12K/15K/20K-T inverter is in a stopped operating state? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator specifications: The GRID indicator is located on the right side of the fourth row of the display panel. An off indicator signifies that the inverter has stopped operation. The following link is a schematic diagram, which shows the position of the indicator in display panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What is the LED indicator descriptions in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Give me the description list of the inverter LED indicator in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator descriptions, including a detailed list of different statuses for all five indicators on the display panel. The following link is a corresponding description list of the inverter LED indicator. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617095957969.png
1. What is the LED indicator descriptions in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Give me an display diagram about the position of inverter LED indicator in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the LED indicator descriptions. The following link is a schematic diagram of brief display explanations. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100449730.jpg
1. What grid structure types does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter support? 2. What are the neutral-to-ground voltage requirements for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter under TT grid configuration? 3. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter support TN-C-S grid connection? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The supported grid structures are: TN-S, TN-C, TN-C-S, TT.Note: For TT configuration, the RMS voltage between neutral and ground must be <20V. The following link is a schematic diagram of supported grid structures. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250617100958127.png
1. What are the interfaces and functions of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product features the following interfaces and functions: INV Logger A200 , RS485 Interface , RS485/CAN (Controller Area Network) Interfaces, Modbus RTU, Export active power control, Multifunction Relay, Temperature Senser Interface, The communication interface for external central grid protection device, Inverter demand response modes (DRED), Ripple control receiver interface, Current transformer interface, Back-up function and Earth fault alarm.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the INV Logger A200 interface? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product comes standard with an INV Logger A200, which provides a user interface for configuration and monitoring. The INV Logger A200 can connect to the internet via WLAN or Ethernet cable.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include RS485 interface? 2. Details about RJ45 ports. 3. what is Terminal block 2? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product equipped with several RS485 interfaces. Some RS485 interfaces connected through RJ45 ports. Some RS485 interfaces connected through terminal block. (1) RJ45-1 and RJ45-2 ports: Two RS485 interfaces used to the product parallel operation. The monitoring information of all the slave inverters can exchange with the master inverter through the RS485 interfaces. And the master inverter transfers the monitoring information to Internet through the INV Logger A200. (2) RJ45-3 port: This RS485 interface used to connect the product to the third-party monitor device. If you don’t want to use INV Logger A200, the third-party monitor device can be used. (3) Terminal block 2 : This RS485 interface (Pin1 and Pin2) used to connect the external smart meter. If the smart meter be chosen to replace the current transformer, the smart meter can connect to this RS485 interface. The following link is a schematic diagram of RS485 interfaces. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618141703896.png
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the RS485 interface? 2. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the CAN interface? 3. Details about RJ45 ports. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product equipped with several RS485/CAN interfaces. The CAN interfaces and RS485 interfaces connected through one RJ45 ports. (1) RJ45-4 port: This RS485/CAN interface used to connect the BMS (Battery Manage System) of the battery. If the communication interface of the BMS is CAN interface, the pins for CAN interface can be chosen to connect. If the communication interface of the BMS is RS485 interface, the pins for RS485 interface can be chosen to connect. (2) RJ45-5 and RJ45-6 ports: Two RS485/CAN interfaces used to the product parallel operation. The control information can be exchanged between the master inverter and the slave inverter through the RS485/CAN interfaces. Both the pins for RS485 interface and CAN interface shall be chosen to connect. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618141924848.png
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include Modbus RTU? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with a Modbus interface. If the third-party communication device also complies with EnValt Modbus protocol, which can be connected to this product.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include Export active power control? 2. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the current transformers? 3. what is the current transformer duty in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Can I substitute the smart meter for the current transformer in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with the export active power limit function, so as to meet the requirements of some national standards or grid standards for limiting the output power at the grid connection point. The export active power control solution measures the active power at the point where the customer’s installation is connected to the distribution system (point of grid connection) and then uses this information to control the inverter’s output active power in order to prevent the export active power to the distribution system from exceeding the agreed export capacity. The product is delivered with the current transformers as standard. The current transformers can be used to measure the export active power. The communication of the current transformers can be connected to the product through RS485. And the current transformer also can be replaced by the smart meter. The smart meter that can be used with this product must be approved by EnValt. For more information about the smart meter, please contact the service.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the multifunction relay? 2. How many multifunction relays in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with two multifunction relays as standard. The multifunction relays can be configured for the operating mode used by a particular system. For more information, please contact EnValt service.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the temperature senser interface? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with one temperature senser interface. If the temperature of the battery need be monitored, the external senser can be connected.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include the communication interface for external central grid protection device? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with one communication interface to connect the external central grid protection device. For more information, please contact with EnValt service.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include DRED? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product shall detect and initiate a response to all supported demand response commands according to the standard AS/NZS 4777.2. The product only supports the demand response mode DRM 0. The interaction with demand response enabling device (DRED) can be connected to the terminal block 3. The Pin 5 and Pin 6 of the terminal block 3 represents the REF GEN/0 and COM LOAD/0.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include Ripple Control Receiver device? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with one interface to connect Ripple Control Receiver device.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include current transformer? 2. How many current transformers do the FX-5K/6K/8K/10K/12K/15K/20K-T inverter have? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The current transformers can be used to measure the export active power and control the export active power at the point of grid connection. The three current transformers can be connected to terminal block 4.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include Back-up function? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product is equipped with a back-up function which also called as an emergency power supply (EPS). The back-up function ensures that the inverter forms a three-phase back-up grid that uses energy from the battery and the PV system that is directly connected to the inverter to supply the critical load in the event of a utility grid failure. In the event of a grid failure, the product disconnects from the grid. The product provides a standalone grid and the backup loads, which connect to EPS connector, continue to be supplied by the energy stored in the battery and the PV modules. The charging of the battery is ensured by the existing PV system during back-up operation. As soon as the utility grid is available again, the product will automatically connect to the grid and the loads are supplied with energy from the utility grid.
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter include Earth fault alarm? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product complies with IEC 62109-2 clause 13.9 for earth fault alarm monitoring. If an Earth Fault Alarm occurs, the red color LED indicator will light up. At the same time, the error code 38 will be sent to the iEnOS.
1. Is there a schematic diagram for the basic application of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2.After processing solar power, where does the energy from the FX-5K/6K/8K/10K/12K/15K/20K-T inverter go? 3. What exactly is the energy storage function of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. I'd like to learn about the basic system solution for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the basic system solution. The product is a high-quality inverter which can convert solar energy to AC energy and store energy into battery. The product can be used to optimize self-consumption, store in the battery for future use or feed into public grid. The following link is a schematic diagram of basic application. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618152613019.png
1. Is there a schematic diagram for the basic application of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2.After processing solar power, where does the energy from the FX-5K/6K/8K/10K/12K/15K/20K-T inverter go? 3. What exactly is the energy storage function of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Where can I find a detailed description of the basic application of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. I'd like to learn about the basic system solution for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the basic system solution. The product is a high-quality inverter which can convert solar energy to AC energy and store energy into battery. The product can be used to optimize self-consumption, store in the battery for future use or feed into public grid. The following link is a corresponding description list of basic application. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618152749527.png
1. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, are there any special requirements for the neutral wire on the On-grid side and EPS side when installing in New Zealand? 2. Are the grid connection requirements for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter the same in different countries? What precautions should be taken? 3. Where can I find the complete system for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What core energy conversion processes are included in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter's functionality? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the basic system solution. The product is a high-quality inverter which can convert solar energy to AC energy and store energy into battery. The product can be used to optimize self-consumption, store in the battery for future use or feed into public grid. For Australia and New Zealand, the neutral cable of On-grid side and EPS side must be connected together according to the wiring rules AS/NZS 3000. Otherwise the EPS function will not work. The following link is a schematic diagram, which shows the system diagram of this product. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618153851877.png
1. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, are there any special requirements for the neutral wire on the On-grid side and EPS side when installing in New Zealand? 2. Are the grid connection requirements for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter the same in different countries? What precautions should be taken? 3. Where can I find the complete system for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What core energy conversion processes are included in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter's functionality? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the basic system solution. The product is a high-quality inverter which can convert solar energy to AC energy and store energy into battery. The product can be used to optimize self-consumption, store in the battery for future use or feed into public grid. For other countries, grid systems do not have special requirement on wiring connection. The following link is a schematic diagram, which shows the system diagram of this product. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618153851887.png
1. What are the four energy management modes provided by the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What factors determine the energy management modes of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product's Energy Management Mode depends on photovoltaic energy and user preferences, offering four selectable modes: Self-Consumption mode, Back-up mode, User-defined mode, and Off-grid mode.
1. What is the primary optimization objective of the Self-Consumption mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter in Self-Consumption mode, explain how the Energy Management system operates? 3. How does the Self-Consumption mode of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter improve energy self-sufficiency rate? 4. In Self-Consumption mode of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, what are the two basic operational scenarios for nighttime Energy Management? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product's Energy Management Mode depends on photovoltaic energy and user preferences, offering four selectable modes. In Self-Consumption mode, the photovoltaic energy is preferentially used by local load to improve the self- consumption rate and self-sufficiency rate. Here are three cases about the energy management during daytime: (1) PV power generation is lower than the load power consumption, and the energy of the battery is not available. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618155933943.png (2) PV power generation is lower than the load power consumption, and the energy of the battery is available. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618155935458.png (3) PV power generation is larger than the load power consumption. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618160322273.png Here are two cases about the energy management during night: (1) The energy of the battery is available. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618160325796.png (2) The energy of the battery is not available. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618160339510.png
1. What is the primary function of the BAT in Back-up mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Under what conditions does the battery charge in Back-up mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, will the battery discharge when GRID power is available and PV is generating? 4. What three typical energy management scenarios are included in Back-up mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What conditions trigger battery discharge in Back-up mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product's Energy Management Mode depends on photovoltaic energy and user preferences, offering four selectable modes. In back-up mode, the battery is a back-up energy storage device. The battery always charged by PV power if it is not full charged. The battery discharge only when the utility grid loss. Here are three cases about the energy management: (1) The energy of the battery is not full charged. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618161416719.png (2) The energy of the battery is full charged, even at night. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618161421541.png (3) The battery discharge when the utility grid loss. The following link is a schematic diagram of energy management in this scenario. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618161437778.png
1. What are the main characteristics of the User-defined mode in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What does User-defined mode mean? 3. What are the essential requirements for the normal operation of User-defined mode in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Through which channels can users set the charging/discharging schedules in User-defined mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What is the primary difference between User-defined mode and other modes in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product's Energy Management Mode depends on photovoltaic energy and user preferences, offering four selectable modes. In user-defined mode, customers can set their own charging and discharging time periods, and the charging and discharging power can be set by themselves in the APP.
1. Under what grid conditions is it recommended to use Off-grid mode for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the primary purpose of switching to Off-grid mode in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, what action should users take when the grid is unstable? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The product's Energy Management Mode depends on photovoltaic energy and user preferences, offering four selectable modes. In off-grid mode, If the power grid is too weak and the inverter operating unstablely, it is recommended that the customer switch to off grid mode to achieve stable power supply.
1. Can the FX-5K/6K/8K/10K/12K/15K/20K-T inverter have a parallel function? 2. What is the description of parallel system in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Can the parallel system keep working When the gird loss occasionally? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Parallel System. The hybird inverter can operate as a parallel system. The system can even work when the utility grid is loss occasionally. The following link is a schematic diagram of Parallel System. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618165050413.png
1. What is the four FX-5K/6K/8K/10K/12K/15K/20K-T inverters parallelling? 2. When my four FX-5K/6K/8K/10K/12K/15K/20K-T inverters in parallel, how does eps load work? 3. What is the smart meter type of parallel system in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. When my four FX-5K/6K/8K/10K/12K/15K/20K-T inverters in parallel, what is the demand for battery? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Parallel System. Four hybrid inverters with the same model can be connected in parallel in grid port. the EPS load should be independent of each inverter and the battery should be same model and module quantity. The smart meter type of parallel system can be SDM630 modbus V2 (MAX 100Arms) or SDM630MCT V2 with three ESCT-T24 CT (MAX 250Arms), customer can install the different type meter which can meet AC bus current requirement. The following link is a schematic diagram, which shows specific operation of four hybrid inverters parallelling in the same model. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250618171105168.png
1. What is the notice of Parallel System in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the notice of Parallel system wiring in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the notice of adding inverters or deleting inverters in the parallel system in FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the notices of Parallel System. The following link is the notice of Parallel system wiring. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619091621701.png The following link is the notice of adding inverters or deleting inverters in the parallel system. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619092038704.png
1. What are the potential hazards when wall-mounting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-Tinverter. Below are the critical safety warnings regarding wall-mounting requirements for this product. Please read them carefully. The following link is a danger notice of mounting. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_danger.png
1. What recommendations do you have for wall-mounting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What environmental factors should be avoided when wall-mounting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What special precautions should be taken when wall-mounting multiple FX-5K/6K/8K/10K/12K/15K/20K-T inverters? 4. What load-bearing capacity standard is required for the wall-mounting surface of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What is the maximum recommended ambient temperature for wall-mounting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter?？ | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the recommended wall-mounting guidelines for this product: (1) The ambient temperature is recommended below 40°C to ensure optimal operation. (2) A solid support surface must be available (e.g., concrete or masonry). Ensure that the installation surface is solid enough to bear four times the weight. When mounted on drywall or similar materials, the product emits audible vibrations during operation which could be perceived as annoying. (3) The mounting location must be inaccessible to children. (4) The mounting location should be freely and safely accessible at all times without the need for any auxiliary equipment (such as scaffolding or lifting platforms). Non-fulfillment of these criteria may restrict servicing. (5) The mounting location must not be exposed to direct solar irradiation. If the product is exposed to direct solar irradiation, the exterior plastic parts might age prematurely and overheating might occur. When becoming too hot, the product reduces its power output to avoid overheating. The following link is a schematic diagram of this recommendation. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_suggestion.png (6) Never install the inverter horizontally, or with a forward / backward tilt or even upside do- wn. The horizontal installation can result in damage to the inverter. The following link is a schematic diagram of this recommendation. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_angle.png (7) Maintain the recommended clearances to wall as well as to other inverters or objects. The following link is a schematic diagram of this recommendation. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_distance.png (8) In case of multiple inverters, reserve specific clearance between the inverters. The following link is a schematic diagram of this recommendation. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_invs.png (9) The product should be mounted such that the LED signals can be read off without difficulty. (10) The DC load-break switch of the product must always be freely accessible.
1. What warning notices should be observed when handling/relocating the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the key procedural steps for unpacking and handling the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the instructions for unpacking and handling the product from its packaging box: Open the inverter packaging box, take the inverter out of the packaging box, and place the inverter at the designated installation location. The following link is a caution of this operation. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/takeout_move.png
1. What are the wall-mounting installation steps for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the initial positioning requirements for the mounting bracket when wall-mounting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What technical parameters require special attention when drilling for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter wall-mounting? 4. What are the specific steps for securing the mounting bracket in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter installation? 5. How to ensure proper hanging alignment of the inverter on the mounting rack for the FX-5K/6K/8K/10K/12K/15K/20K-T? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The following are the wall-mounting installation steps for this product: (1) Align the mounting-bracket horizontally on the wall with the arrow upwards. Mark the position of the drill hole. Set the wall mounting bracket aside and drill the marked holes with the diameter of 10mm. The depth of the holes should be about 70 mm. Keep the hammer drill bit perpendicular to the wall to avoid drilling inclined. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_s1.png (2) Hammer the plastic expansion pipe slowly into the drilled hole. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_s2.png (3) Align the mounting-bracket with the hole position and use the tapping nail to fix the hanging plate. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/mounting_s3.png (4) Hang the inverter to the mounting-bracket and ensure that the mounting ears perfectly engage with the mounting-bracket. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619095655424.png (5) Fix the inverter with screws. The following link is a schematic diagram of this step.https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619095700439.png
1. Where is the electrical connection located on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the main components of the electrical connection instructions for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Give me details about electrical connection in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 4. For FX-5K/6K/8K/10K/12K/15K/20K-T inverter, how about the DC switch in the Australian market? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Electrical connection of the product. The following link is a schematic diagram, which shows a connection port description of the inverter's bottom panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619102153433.png The following link is a schematic diagram of the DC switch for the Australian market. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619102158677.png Notice: Figure shown here is for reference only. The actual product received may differ！
1. What are the main components of the electrical connection instructions for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Give me description list of connection port in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter's bottom panel. 3. Give me details about electrical connection in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Electrical connection of the product. The following link is a corresponding description list of connection port in the inverter's bottom panel. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619102209082.png
1. Is the FX-5K/6K/8K/10K/12K/15K/20K-T inverter equipped with a grounding conductor monitoring device? 2. What is the main function of the grounding conductor monitoring device in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Is additional grounding connection mandatory for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? What conditions determine this requirement? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Connecting additional grounding of the product. The inverter is equipped with a grounding conductor monitoring device. This grounding conductor monitoring device detects when there is no grounding conductor connected and disconnects the inverter from the utility grid if this is the case. Hence the product does not require an additional grounding or equipotential bonding when operating. Notice: If the grounding conductor monitoring function is deactivated or the additional grounding is required by locally standard, you can connect additional grounding to the inverter.
1. What are the detailed requirements for the secondary protection ground cable of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements for the secondary protection ground cable. The following link is a corresponding description list of the requirements for the secondary protection ground cable. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/additional_grounding_require.png
1. What are the installation steps for the secondary protection ground cable on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What is the final anti-corrosion procedure for grounding terminal installation in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What tools are required to secure the grounding terminal in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the procedure of secondary protection ground cable: (1) Strip the grounding cable insulation. Insert the stripped part of the grounding cable into the ring terminal lug and crimp using a crimping tool. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/additional_grounding_s1.png (2) Remove the screw on the ground terminal, insert the screw through the OT/DT terminal, and lock the terminal using a wrench. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619103646061.png (3) Apply paint to the grounding terminal to ensure corrosion resistance.
1. What standards must the grid cables meet for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What standards must the grid cables meet for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What determines the minimum conductor size for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What determines the minimum conductor size for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What key factors should be considered when selecting grid cables for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 6. What key factors should be considered when selecting grid cables for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 7. Where can I find the specific cable requirements for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 8. Where can I find the specific cable requirements for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. The cable must be dimensioned in accordance with the local and national directives for the dimensioning of cables. The requirements for the minimum wire size derive from these directives. Examples of factors influencing cable dimensioning are: nominal AC current, type of cable, routing method, cable bundling, ambient temperature and maximum desired line losses. The following link is a schematic diagram of cable. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619105027336.png
1. What standards must the grid cables meet for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What standards must the grid cables meet for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What determines the minimum conductor size for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What determines the minimum conductor size for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What key factors should be considered when selecting grid cables for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 6. What key factors should be considered when selecting grid cables for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 7. Where can I find the specific cable requirements for Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 8. Where can I find the specific cable requirements for EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. The cable must be dimensioned in accordance with the local and national directives for the dimensioning of cables. The requirements for the minimum wire size derive from these directives. Examples of factors influencing cable dimensioning are: nominal AC current, type of cable, routing method, cable bundling, ambient temperature and maximum desired line losses. The following link is a corresponding description list of cable. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619105031810.png
1. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter have built-in residual current protection for Grid connection? 2. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter have built-in residual current protection for EPS Load connection? 3. Under what circumstances is additional residual current protection required for Grid connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Under what circumstances is additional residual current protection required for EPS Load connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5.What type of residual current protection device should be selected for Grid connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter if external protection is needed? 6. What type of residual current protection device should be selected for EPS Load connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter if external protection is needed? 7. What is the minimum protection threshold requirement for external residual current protection devices in Grid connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 8. What is the minimum protection threshold requirement for external residual current protection devices in EPS Load connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 9. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter require external residual current protection for Grid connection in standard configuration? 10. Does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter require external residual current protection for EPS Load connection in standard configuration? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. Here is the description of Residual Current Protection。The product is equipped with an integrated universal current-sensitive residual current monitoring unit inside. Hence the product does not require an external residual-current device when operating. Notice: If local regulations require the use of a residual-current device, please install a type A residual-current protection device with a protection limit of not less than 300mA.
1. What is the applicable Overvoltage category standard for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during Grid connection? 2. What level of grid system can the FX-5K/6K/8K/10K/12K/15K/20K-T inverter be permanently connected to during Grid connection? 3. Under what special conditions are additional overvoltage protection measures required for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during Grid connection? 4. What overvoltage protection objectives must be met for long-distance outdoor cable connections when performing Grid connection on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. What is the applicable Overvoltage category standard for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during EPS Load connection? 6. What level of grid system can the FX-5K/6K/8K/10K/12K/15K/20K-T inverter be permanently connected to during EPS Load connection? 7. Under what special conditions are additional overvoltage protection measures required for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during EPS Load connection? 8. What overvoltage protection objectives must be met for long-distance outdoor cable connections when performing EPS Load connection on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a HFX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. Here is the description of overvoltage category. The inverter can be used in grids of overvoltage category III or lower in accordance with IEC 60664-1. That means that the product can be permanently connected to the grid-connection point of a building. In case of installations with long outdoor cable route, additional measures to reduce overvoltage category IV to overvoltage category III are required.
1. Why does each FX-5K/6K/8K/10K/12K/15K/20K-T inverter need a separate AC circuit breaker in a multi-inverter system during Grid connection? 2. What key factors should be considered when selecting the AC circuit breaker rating for Grid connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Under what conditions should the AC circuit breaker rating be reduced for Grid connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Why does each FX-5K/6K/8K/10K/12K/15K/20K-T inverter need a separate AC circuit breaker in a multi-inverter system during EPS Load connection? 5. What key factors should be considered when selecting the AC circuit breaker rating for EPS Load connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 6. Under what conditions should the AC circuit breaker rating be reduced for EPS Load connection with the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. Here is the description of AC circuit breaker. In PV systems with multiple inverters, protect each inverter with a separate circuit breaker. This will prevent residual voltage being present at the corresponding cable after disconnection.No consumer load should be applied between AC circuit breaker and the inverter. The selection of the AC circuit breaker rating depends on the wiring design (wire cross-section area), cable type, wiring method, ambient temperature, inverter current rating, etc. Derating of the AC circuit breaker rating may be necessary due to self-heating or if exposed to heat. The maximum output current and the maximum output overcurrent protection of the inverters can be found in Technical data.
1. What safety monitoring devices are equipped on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during Grid connection? 2. What is the main function of the grounding conductor monitoring device in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during Grid connection? 3. What measures are recommended when uncertain about disabling monitoring functions during Grid connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What safety monitoring devices are equipped on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during EPS Load connection? 5. What is the main function of the grounding conductor monitoring device in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter during EPS Load connection? 6. What measures are recommended when uncertain about disabling monitoring functions during EPS Load connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the requirements of grid cable connection and EPS Load cable connection. Here is the description of Grounding conductor monitoring. The inverter is equipped with a grounding conductor monitoring device. This grounding conductor monitoring device detects when there is no grounding conductor connected and disconnects the inverter from the utility grid if this is the case. Depending on the installation site and grid configuration, it may be advisable to deactivate the grounding conductor monitoring. This is necessary, for example, in an IT system if there is no neutral conductor present and you intend to install the inverter between two line conductors. If you are uncertain about this, contact your grid operator or EnValt.
1. How does the FX-5K/6K/8K/10K/12K/15K/20K-T inverter ensure safety when the grounding conductor monitoring is disabled? 2. What minimum cross-sectional area requirements must the additional grounding meet for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. In order to guarantee safety in accordance with IEC 62109 when the grounding conductor monitoring is deactivated, carry out the following measure. Connect an additional grounding that has at least the same cross-section as the con- nected grounding conductor to the AC cable. This prevents touch current in the event of the grounding conductor on the AC cable failing.
1. What are the detailed steps for assembling the grid connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What indicates the completion of assembling the grid connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What is the Crimping tool selection and crimping requirements in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. What is the sequence of the AC connector cable harness in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 5. Introduction to "Assembling the grid Connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Assembling the grid connectors: (1) Switch off the miniature circuit-breaker or the switch of every energy sources and secure it against being inadvertently switched back on. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132713633.png (2) Split grid connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132720189.png (3) Crimp the terminals with crimping pliers. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132734729.png The following link is a schematic diagram of Crimping tool selection and crimping requirements. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132741135.png (4) Set the parts on the cable, insert the terminal holes in sequence. Crimp the wire with an inner hexagon screwdriver and screw the torque 1.2+/-0.1N·m. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132747648.png (5) Insert the main body into the rubber core and hear the “click” sound. Tighten the nut with an open-ended wrench (torque 2.5±0.5 N·m). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132754239.png (6) Tighten the nut with an open-ended wrench (torque 2.5±0.5 N·m). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132800825.png The following link is a schematic diagram, which shows the sequence of the AC connector cable harness. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619133234496.png
1. What are the detailed steps for Connecting the grid connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What indicates the completion of Connecting the grid connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Introduction to "Connecting the grid Connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Connecting the grid connectors: （1）Remove the dust cover. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619134355275.png （2）The installation arrow indicates insertion the female connector, and hear the “click” sound. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619134410884.png
1. What are the detailed steps for assembling the EPS Load connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What indicates the completion of assembling the EPS Load connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Introduction to "Assembling the EPS Load Connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Assembling the EPS Load connectors: (1) Switch off the miniature circuit-breaker or the switch of every energy sources and secure it against being inadvertently switched back on. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132713633.png (2) Split grid connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132720189.png (3) Crimp the terminals with crimping pliers. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132734729.png The following link is a schematic diagram of Crimping tool selection and crimping requirements. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132741135.png (4) Set the parts on the cable, insert the terminal holes in sequence. Crimp the wire with an inner hexagon screwdriver and screw the torque 1.2+/-0.1N·m. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132747648.png (5) Insert the main body into the rubber core and hear the “click” sound. Tighten the nut with an open-ended wrench (torque 2.5±0.5 N·m). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132754239.png (6) Tighten the nut with an open-ended wrench (torque 2.5±0.5 N·m). https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619132800825.png
1. What are the detailed steps for Connecting the Back Load connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What indicates the completion of Connecting the Back Load connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Introduction to "Connecting the Back Load Connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. 4. Introduction to "Connecting the EPS Load Connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Connecting the Back Load connectors: （1）Remove the dust cover. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619134710211.png （2）The installation arrow indicates insertion the female connector, and hear the “click” sound. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619134721273.png
1. What are the Requirements for the PV modules per input in the DC connection of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the Requirements for the DC connection, specifically the Requirements for the PV modules per input: (1) All PV modules should be of the same type. (2) All PV modules should be aligned and tilted identically. (3) On the coldest day based on statistical records, the open-circuit voltage of the PV modules must never exceed the maximum input voltage of the inverter. (4) The maximum input current per PV module must be maintained and must not exceed the through fault current of the DC connectors. (5) The connection cables to the inverter must be equipped with the connectors included in the scope of delivery. (6) The thresholds for the input voltage and the input current of the inverter must be adhered to. (7) The positive connection cables of the PV modules must be equipped with the positive DC connectors. The negative connection cables of the PV modules must be equipped with the negative DC connectors.
1. What hazards should I be aware of when assembling the DC connectors for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is a critical safety warning regarding Assembling the DC connectors. Please read carefully. The following link is a schematic diagram of warning notice. 1.https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_dc_danger.png
1. How many different types of DC connectors might the FX-5K/6K/8K/10K/12K/15K/20K-T inverter be equipped with? 2. For the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, provide me with some description regarding assembling the DC connectors. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the description for assembling the DC connectors: To connect to the inverter, all PV module connection cables must be paired with the provided DC connectors. Note: There may be one of two different types of DC connectors.
1. What does the Type 1 DC connector look like in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? Please describe its appearance. | This is the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, the following describes the Type 1 DC connector when assembling the DC connectors. The following link is a schematic diagram, which shows the description of Type 1 DC connector. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc.png
1. What are the cable requirements for the Type 1 DC connector in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the cable requirements for the Type 1 DC connector when assembling the DC connectors. The following link is a corresponding description list of cable requirements for the Type 1 DC connector. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc_list.png
1. How is the Type 1 DC connector assembled in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the assembling progress for the Type 1 DC connector when assembling the DC connectors. Be sure to observe the correct polarity. The DC connectors are marked with the symbols “+” and “-”. Here are the steps: （1）Strip 12 mm off the cable insulation. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc_s1.png （2）Crimp the contacts with the corresponding cables. Crimping tool: PV-CZM-61100. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc_s2.png Notice: If the stranded wire is not visible in the chamber, the cable is not correctly inserted and the connector must be reassembled. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc_s2_.png （3）Push the swivel nut up to the thread and tighten the swivel nut. (SW15, Torque: 2.0Nm) The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_1dc_s3.png
1. What does the Type 2 DC connector look like in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? Please describe its appearance. | This is the FX-5K/6K/8K/10K/12K/15K/20K-T inverter, the following describes the Type 2 DC connector when assembling the DC connectors. The following link is a schematic diagram, which shows the description of Type 2 DC connector. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_2dc.png
1. What are the cable requirements for the Type 2 DC connector in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the cable requirements for the Type 2 DC connector when assembling the DC connectors. The following link is a corresponding description list of cable requirements for the Type 2 DC connector. 1. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_2dc_list.png
1. How is the Type 2 DC connector assembled in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the assembling progress for the Type 2 DC connector when assembling the DC connectors. Be sure to observe the correct polarity. The DC connectors are marked with the symbols “+” and “-”. Here are the steps: （1）Strip 12 mm off the cable insulation. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_2dc_s1.png （2）Assemble the cable ends with the crimping pliers. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_2dc_s2.png （3）Lead the cable through cable gland, and insert into the insulator until it snaps into place. Gently pull the cable backward to ensure firm connection. Tighten the cable gland and the insulator (Torque 2.5-3Nm). The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/assemble_2dc_s3.png （4）Ensure that the cable is correctly positioned.
1. What precautions should be taken when connecting the PV module to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What danger warnings and caution notices apply when connecting the PV module to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are a danger warning and a caution notice for connecting the PV module. The following link is a schematic diagram of a danger warning for connecting the PV module. 1、https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_danger.png 2、The following link is a schematic diagram of a caution notice for connecting the PV module. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_notice.png
1. What are the steps for connecting PV modules to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. How to correctly connect Type 1 DC connectors to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. How to correctly connect Type 2 DC connectors to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Introduction to "Connecting the PV module" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of connecting the PV module: （1）Ensure that the individual miniature circuit-breaker is switched off and ensure that it cannot be accidentally reconnected. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s1.png （2）Ensure that the DC switch is switched off and ensure that it cannot be accidentally reconnected. （3）Ensure that there is no ground fault in the PV array. （4）Check whether the DC connector has the correct polarity. Notice: If the DC connector is equipped with a DC cable having the wrong polarity, the DC connector must be reassembled. The DC cable must always have the same polarity as the DC connector. （5）Ensure that the open-circuit voltage of the PV array does not exceed the maximum DC input voltage of the inverter. （6）Connect the assembled DC connectors to the inverter until they audibly snap into place. （6a）First, connect the assembled DC connectors to the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s6a_1.png Second, for unused DC connectors, push down the clamping bracket and push the swivel nut up to the thread. Insert the DC connectors with sealing plugs into the corresponding DC inputs on the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s6a_2.png Third, Insert the DC connectors with sealing plugs into the corresponding DC inputs on the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s6a_3.png （6b）First, Connect the assembled DC connectors to the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s6b_1.png Second, for unused DC connectors, push down the clamping bracket and push the swivel nut up to the thread. Insert the DC connectors with sealing plugs into the corresponding DC inputs on the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619153406234.png The following link is a schematic diagram of a notice. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/connect_pv_s6b_2_.png （7）Ensure that all DC connectors and the DC connectors with sealing plugs are securely in place.
1. What are the specific requirements for battery connection cables in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What cable specifications are required when connecting batteries to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What special precautions should be taken when installing battery connection cables in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Provide a schematic diagram of the battery cables. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the Requirements for the Battery connection, specifically the Cable Requirements. The following link is a schematic diagram of Battery connector. 1、https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619155211664.png
1. What are the specific requirements for battery connection cables in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What cable specifications are required when connecting batteries to the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. What special precautions should be taken when installing battery connection cables in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 4. Provide a schematic diagram of the battery cables. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the Requirements for the Battery connection, followed by the detailed Cable Requirements list. The following link is a corresponding description list of detailed Cable Requirements. 1、
1. What is the procedure for assembling the battery connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Introduction to "Assembling the Battery connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Assembling the Battery connectors: （1）Strip 6-7.5 mm off the cable insulation. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619160845593.png （2）Assemble the cable ends with the crimping pliers. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619160850071.png （3）Lead the cable through cable gland, and insert into the insulator until it snaps into place. Gently pull the cable backward to ensure firm connection. Tighten the cable gland and the insulator (Torque 4Nm). The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619160854566.png （4）Ensure that the cable is correctly positioned.
1. What is the procedure for Connectling the battery connectors on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Introduction to "Connecting the Battery connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Connecting the Battery connectors: （1）Remove the dust and waterproof cover of the BMS connector on the inverter and retain it. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619161642819.png （2）Connect the assembled DC connectors to the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619161649271.png
1. What are the steps for the INV-Logger of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Are there any precautions when connecting the INV-Logger in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Introduction to "Connecting the Battery connectors" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of INV Logger A200 connection: （1）Rotate the nut, take out the sealing ring, hold the locking structure, and take out the wiring terminal. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163007378.png （2）Lock the communication cable to the wiring terminal according to the sequence shown in the following figure. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163012602.png （3）Insert the wiring terminal into the sealing head, adjust the communication cable, insert the sealing ring, and locknut. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163017098.png （4）Remove the dust and waterproof cover of the INV Logger A200 on the inverter and retain it. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163027141.png （5）Attach the INV Logger A200 to the connection port in place and tighten it into the port by hand with the nut in the modular. Make sure the modular is securely connected and the label on the modular can be seen. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163036936.png The following link is a schematic diagram of a notice. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619163226010.png
1. What about the Communication interface description in the FX-5K/6K/8K/10K/12K/15K/20K-T Inverter? 2. Does FX-5K/6K/8K/10K/12K/15K/20K-T Inverter have communication interfaces? 3. Give some information about the interface configuration of the communication interface. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Communication equipment connection. Here is the Communication interface description. The inverter is equipped with a communication interface, which is used to connect communication cables such as lithium battery, electricity meter and parallel machine. The following link is a schematic diagram of the interface configuration of the communication interface. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619164423814.png 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619164557412.png 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619164601684.png
1. What is the procedure for Communication cable connection on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Introduction to " Communication cable connection" in the Wiring Procedure of FX-5K/6K/8K/10K/12K/15K/20K-T Inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Communication cable connection: (1) Remove the communication cover. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165246172.png (2) Route the communication cable through the communication cover and crimp the wiring terminal. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165252662.png (3) Connect the communication cable crimped to the corresponding communication port. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165300615.png (4) Install the communication cover on the inverter. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165306064.png (5) Tighten the cable gland nuts. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165310790.png
1. What is the schematic diagram of Current Transformer connection on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The following link is a schematic diagram of Current Transformer connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165707934.png
1. What is the schematic diagram of Smart meter connection on the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What network architecture is supported for Smart meter connection in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The following link is a schematic diagram of Smart meter connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619165904442.png Notice: The grid structure supported by the product is TN-S.
1. What aspects need to be checked before starting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. I need to commission my FX-5K/6K/8K/10K/12K/15K/20K-T inverter - what should I pay attention to beforehand? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Inspection before commissioning of the product. The following link is a schematic diagram, which shows a danger warning and the checklist items for pre-startup inspection of the INV. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/inspection.png Here are the aspects need to be checked before starting: (1) Make sure the inverter DC switch and external circuit breaker are disconnected. (2) Make sure the inverter has been correctly mounted with wall bracket. (3) Make sure nothing is left on the top of the inverter. (4) Make sure the communication cable and AC connector have been correctly wired and tightened. (5) Make sure the inverter’s exposed metal surface has a ground connection. (6) Make sure the DC voltage of the strings does not exceed the permitted limits of the inverter. (7) Make sure the DC voltage has the correct polarity. (8) Make sure that the insulation resistance to ground is greater than the insulation resistance pro- tection value. (9) Make sure the grid voltage at the point of connection of the inverter complies with the permitted value of the inverter. (10) Make sure the AC circuit breaker complies with this manual and all applicable local standards.
1. What is the commissioning procedure for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. When can the EPS and grid port circuit breakers be closed during the commissioning procedure of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 3. Which parameters of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter can be configured via mobile device during commissioning? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the steps of Commissioning procedure: (1) Turn the DC switch of the inverter to “ON” position and start battery, but keep the breakers on EPS and grid port to "OFF" position. (2) Connect the inverter with HANCHU iESS APP, For details. Then set grid code, operation mode, merter or CT type, battery model and SOC limi. (3) Turn the breakers on EPS and grid port to "ON" position. If the irradiation and grid conditions meet requirements, the inverter will operate normally. (4) Observe the LED indicator to ensure inverter operates normally, check the inverter and battery parameters in APP.
1. Which connectors need to be removed in sequence when disconnecting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the steps for disconnecting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter from voltage sources? 3. What precautions should be taken when disconnecting the FX-5K/6K/8K/10K/12K/15K/20K-T inverter from voltage sources? 4. What the steps for disconnecting all electrical connections in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is disconnecting all electrical connections. Prior to performing any work on the product, always disconnect it from all voltage sources as described in this section. Always adhere to the prescribed sequence. The following link is a schematic diagram of a warnning. 1.https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619173024437.png Below is the steps of Disconnecting the inverter from voltage sources: （1）Disconnect the miniature circuit breaker and secure against reconnection. （2）Disconnect the DC switch and secure against reconnection. （3）Wait until the LEDs have gone out. （4）Use a current clamp meter to ensure that no current is present in the DC cables. The following link is a schematic diagram of a warnning. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/disconnect_danger.png （5）Loosen and remove the DC connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/disconnect_dc.png （6）Ensure that no voltage is present between the positive terminal and negative terminal at the DC inputs using a suitable measuring device. （7）Loosen and remove the Grid connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619172604982.png （8）Loosen and remove the EPS Load connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619172609120.png （9）Loosen and remove the Battery connector. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619172618051.png （10）Remove the communication cover. （11）Hold down the buckle on the side of the INV Logger A200 and pull out the INV Logger A200 terminal. The following link is a schematic diagram of this step. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250619172621379.png
1. What are the steps for dismantling the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What precautions should be taken when dismantling the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. After disconnecting all electrical connections, below is the steps of dismantling the inverter: (1) Dismantle the inverter referring to “Mounting” in reverse steps. (2) If necessary, remove the wall-mounting bracket from the wall. (3) If the inverter will be reinstalled in the future, please refer to “Product Storage” for a proper conservation.
1. I would like to know the technical data for different power ratings of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 2. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of DC input? 3. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of AC input and output? 4. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of battery data? 5. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of EPS load data? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different power models (HESS-HY-T-05/06/08/10/12K), including DC input, AC input and output, efficiency, battery data, and EPS load data. The following link is a corresponding description list of technical data. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623092612355.png The following link is a corresponding description list of technical data. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623092638878.png The following link is a corresponding description list of technical data. 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623092647745.png The following link is a corresponding description list of technical data. 4. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623092651517.png Notice: (1) The voltage range meets the requirements of the corresponding national grid code. (2) The frequency range meets the requirements of the corresponding national grid code.
1. I would like to know the technical data for different power ratings of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 2. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of DC input? 3. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of AC input and output? 4. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of battery data? 5. In FX-5K/6K/8K/10K/12K/15K/20K-T, what is the Technical data of EPS load data? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different power models (HESS-HY-T1-05/06/08/10/12K), including DC input, AC input and output, efficiency, battery data, and EPS load data. The following link is a corresponding description list of technical data. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623093540821.png The following link is a corresponding description list of technical data. 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623093547164.png The following link is a corresponding description list of technical data. 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623093553049.png The following link is a corresponding description list of technical data. 4. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623093601375.png Notice: (1) The voltage range meets the requirements of the corresponding national grid code. (2) The frequency range meets the requirements of the corresponding national grid code.
1. Introduce the general data in the FX-5K/6K/8K/10K/12K/15K/20K-T series. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different models (FX-5K/6K/8K/10K/12K/15K/20K-T), followed by General data. The following link is a corresponding description list of technical data. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623094220853.png
1. Introduce the general data in the FX-5K/6K/8K/10K/12K/15K/20K-T series. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different models (FX-5K/6K/8K/10K/12K/15K/20K-T), followed by General data. The following link is a corresponding description list of technical data. 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623094220853.png
1. Introduce the protective function in the FX-5K/6K/8K/10K/12K/15K/20K-T series. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different models (FX-5K/6K/8K/10K/12K/15K/20K-T), followed by Protective function. The following link is a corresponding description list of technical data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623094227809.png
1. Introduce the protective function in the FX-5K/6K/8K/10K/12K/15K/20K-T series. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the technical data for different models (FX-5K/6K/8K/10K/12K/15K/20K-T), followed by Protective function. The following link is a corresponding description list of technical data. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/HESS-HY-T-5~12K/20250623094227809.png
1. What are the danger warnings for cleaning the contacts of the DC switch in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the relevant steps for cleaning the contacts of the DC switch in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Maintenance of the product. The following link is a schematic diagram of a danger notice in cleaning the contacts of the DC switch. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/maintenance_danger.png Here are the steps of the cleaning the contacts of the DC switch: (1) Disconnect the AC disconnector and prevent accidental restart. (2) Rotate the DC switch handle from the “ON” position to the “OFF” position for 5 times.
1. What are the caution warnings for cleaning air inlet and outlet in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. What are the relevant steps for cleaning air inlet and outlet in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the Maintenance of the product. The following link is a schematic diagram of a caution notice in cleaning air inlet and outlet. https://oss-cdn.hanchuess.com/Knowledge_data_base/user_manual/HESS-HY-S-3~6K/maintenance_caution.png Here are the steps of the cleaning air inlet and outlet: (1) Disconnect the AC side circuit breaker and ensure that it cannot be accidentally reconnected. (2) Disconnect the DC switch, rotate the DC switch handle from the “ON” position to the “OFF” position. (3) Clean the air inlet and outlet of the inverter with a soft brush.
1. What are the disposal principles for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter and its components? 2. Can the FX-5K/6K/8K/10K/12K/15K/20K-T inverter be discarded arbitrarily? 3. I would like to know about the recycling and disposal of the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below are the recycling and disposal guidelines for this product: Dispose of packaging and replaced components according to applicable regulations in the country of installation. Note: Do not dispose of this product with household waste, but handle it in accordance with applicable e-waste regulations.
1. What is the EU declaration of conformity for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? 2. Where can the full EU declaration of conformity for the FX-5K/6K/8K/10K/12K/15K/20K-T inverter be found? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. Below is the EU declaration of conformity: Within the scope of EU directives - Radio Equipment Directive 2014/53/EU (L 153/62-106, 22.05.2014) (RED), Restriction of Hazardous Substances 2011/65/EU (L 174/88, 08.06.2011) and 2015/863/EU (L 137/10, 31.03.2015) (RoHS), Jiangsu Hanchu Energy Technology Co., LTD declares that the inverter described in this manual complies with the essential requirements and other relevant provisions of the above directives. Note: The full EU declaration of conformity can be found at www.hanchuess.com.
1. Introduction to the wiring diagram of EPS in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter. 2. What is the wiring diagram for inverter EPS in the FX-5K/6K/8K/10K/12K/15K/20K-T inverter? | This is a FX-5K/6K/8K/10K/12K/15K/20K-T inverter. The following link is a schematic diagram, which shows the wiring diagram for EPS in three phase inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250630140141880.png