## Sheet1
问题 | 答案
1. Can the EBS-H-5.3K battery be installed outdoors during a thunderstorm or snowy weather? 2. Is it allowed to open the panel of the EBS-H-5.3K battery for maintenance? 3. What should I do if I discover a fire near the EBS-H-5.3K battery system? 4. Can I lift or transport the EBS-H-5.3K battery by its terminals or bolts? 5. Do I need to measure voltage before touching the terminals of the EBS-H-5.3K battery? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the general requirements carefully. It is strictly prohibited to install or operate outdoor equipments and cables (including handling equipment, operating equipment and cables, plugging and unplugging signal interfaces connected to the outdoors, working at heights, outdoor installation, etc.) in severe weather such as thunderstorm, snowy weather, strong breeze. Please observe the operation sequence and safety precautions in this manual and other related manuals. Follow the warning signs, cautions and precautions on the equipment. Follow the manual to use correct tools, and master the correct use of tools. Do not install and connect cables, maintain, or replace equiprments with power on. Do not wash the equipment. Do not open the panel of the equipment. Measure the voltage before touching conductor surface or terminal to verify that there is no risk of electric shock. Repair the scratches that occur during equipment transportation and installation in time. It is strict forbidden to expose the scratched parts to the outdoor environment for a long time. It is forbidden to lift and transport the batteries through the battery terminals or bolts. Do not alter the internal structure or installation procedure of the equipment without prior permission of the manufacturer. Leave the building or the equipment area and turn on the fire alarm bell or make an emergency call immediately in the case of a fire. Do not enter the building on fire in any case.
1. Who is allowed to install or maintain the EBS-H-5.3K battery—can regular technicians do it, or does it require certified professionals? 2. Does the EBS-H-5.3K battery require special certifications for high-voltage operations, and if so, which ones? 3. Can an operator (non-trained personnel) perform basic maintenance on the EBS-H-5.3K battery, or must it always be done by a professional? 4. Who is authorized to replace components or software in the EBS-H-5.3K battery? 5. What is the difference between a 'professional' and 'trained personnel' for handling the EBS-H-5.3K battery? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the personnel requirements carefully. Personnel installing or maintaining EnValt equipment must be trained, understand all necessary safety precautions, and be able to correctly perform all operations. Personnel who will operate the equipment, including operators, trained personnel and professionals should possess local national required qualifications in special operations such as high-voltage operations and operations of special equipment. Only qualified professionals or trained personnel are allowed to install, operate and maintain the equipment. Only qualified professionals are allowed to remove security facilities and overhaul equipment. Only professionals or authorized personnel are allowed to replace the equipment or components (including software). Professionals: personnel who are trained or experienced in equipment operations and are clear of the sources and degree of various potential hazards in equiprment installation, operation and maintenance. Trained personnel: personnel who are technically trained, have required experience, are aware of possible hazards on themselves in certain operations and are able to take protective measures to minimize the hazards on themselves and other people. Operators: operation personnel who may come into contact with the equipment, except trained personnel and professionals.
1. Can the EBS-H-5.3K battery be installed outdoors in coastal areas within 500m of the sea? 2. Is wall-mounting mandatory for basement installations of the EBS-H-5.3K battery? 3. What minimum safety clearance is needed between the EBS-H-5.3K battery and vehicle traffic in a garage? 4. Are there restrictions on installing the EBS-H-5.3K battery near water pipes or sprinklers? 5. Does the EBS-H-5.3K battery require additional cooling if installed in direct sunlight? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the installation environment requirements carefully. This does not apply to equipment intended to be installed in restricted access areas. The installation and operating environment must comply with international, national and local standards for lithium batteries and with local laws and regulations. Install in a location out of the reach of children. Garage installation needs to be far away from the direction of vehicle travel, it is recommended to install the energy storage on the wall above the body bumper to avoid an accidental collision. When installing the battery in a basement, keep good ventilation. Do not place flammable or explosive materials around the battery. It is recommended that the battery be mounted on the wall to avoid contacting with water. Install the battery in a dry and well-ventilated environment. Secure the battery on a solid and flat surface. Install the battery in a sheltered place or install an awning over it to avoid direct sunlight or rain. Install the battery in a clean environment that is free from sources of strong infrared radiation, organic solvents, and corrosive gases. Precautions should be taken for installation in areas with firequent natural disasters such as floods, mudslides, earthquakes and typhoons. Keep the battery away from fire sources. Do not place any flarmmable or explosive materials around the battery. Keep the battery away from water sources such as taps, sewer pipes, and sprinklers to prevent water seepage. Do not install the battery in a position where it is easy to touch as the temperature of the chassis and heat sink is high when the battery is running. To prevent fire due to high temperature, ensure that the vents aand the cooling system are not blocked when the battery is running. Do not expose the battery to flammable, explosive gas or smoke. Do not perform any operation on the battery in such an environment. Do not install the battery on a moving object, such as ship, trainor car. Do not install the system outdoors in a salt-affected area because the system may be corroded. A salt affected area is an area within 500m from the coast or affected by sea breeze. The area affected by the sea breeze varies according to meteorological conditions (succh as typhoons and seasonal winds) or topographical conditions (such as DAMS and hills).
1. Can I connect or disconnect DC cables while the EBS-H-5.3K battery is powered on? 2. What is the minimum required distance between cables and heat sources for the EBS-H-5.3K battery? 3. Is it safe to install the EBS-H-5.3K battery’s cables in sub-zero temperatures? 4. Do I need special tools for high-voltage work on the EBS-H-5.3K battery? 5. How do I verify if my prepared cables comply with the EBS-H-5.3K battery’s requirements? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the electrical requirements carefully. 1. General Requirements Before connecting cables, ensure that the product is intact. Otherwise, electric shocks or fire may occur. Ensure that all electrical connections comply with local electrical standards. Ensure that the cables you prepared meet local regulations. Use dedicated insulated tools when performing high-voltage operations. 2. DC Operation Do not connect or disconnect power cables with power-on. Transient contact between the core of the power cable and the conductor will generate electric arcs or sparks, which may cause fire or personal injury. Before connecting cables, cut off the power supply if people may corntact energized components. Please ensure that the label on the power cable is correct before connecting the power cord. Disconnect all inputs and operate the equipment only after the equipment is powered off. 3. Cabling Requirements When routing cables, ensure that a distance of at least 301mm exists between the cables and heat-generating components or areas. This prevents damage of the insulation layer of the cables. When the temperature is low, violent impact or vibration may damage the plastic cable sheathing. To ensure safety, comply with the following requirements: Cables can be laid or installed only when the temperature is higher than 0°C. Handle cables with caution especially at a low temperature. If the storage environment temperature of the cables is below 0°C, the cables must be stored at room temperature for more than 24 hours before laying the cables.
1. What personal protective equipment (PPE) is mandatory when handling the EBS-H-5.3K battery? 2. Can I touch the battery casing while the EBS-H-5.3K battery is operating? 3. What should I do if the EBS-H-5.3K battery leaks electrolyte? 4. Is grounding required before using the EBS-H-5.3K battery system? 5. What are the critical precautions when connecting/disconnecting the EBS-H-5.3K battery terminals? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the personal safety requirements carefully. Wear proper personal protective equipment during operation. If there is a probability of personal injury or equipment damage, stop the operations and take feasible protective measures immediately. Use tools correctly to avoid hurting people or damaging the equipmeent. The anti-static gloves must be worn when touching the equipmhent. Do not wear clothes that can easily generate static electricity. Do not touch the shell when the equipment is running, the termperature of the shell is high, which may cause burns. To ensure personal safety and normal use, it should be groundeed reliably before use. When the battery is faulty, the temperature may exceed the burn threshold of the touchable surface. Therefore, avoid touching the battery. The electrolyte is harmful to your skin and eyes, so do not disassemble or damage the battery and avoid contact with the electrolyte. Do not place irrelevant objects on the top of the equipmentor insert them into any position of the equipment. Do not place flammable objects around the equipment. To prevent explosions and body injuries, do not place batteriesin a fire. Do not place the battery module in water or other liquids. Do not short-circuit the battery terminals or it will cause afire. Do not use water to clean electrical components inside or outside of a cabinet. Do not stand, rely or sit on the equipment. Do not destroy any module of the equipment. Batteries may cause electric shocks and high short-circuit currents. When using the battery, pay attention to the following points: a) Remove all metal objects from yourself, such as watches and rings. b) Use tools with insulated handles. c) Wear rubber gloves and boots. d) Do not put tools or metal parts on the top of the battery. e) Disconnect the charging power supply before connecting or disconnecting the battery terminal. f) Determine if the battery is unexpectedly grounded. Please remove power from the ground if accidental grounding occurs.
1. What are the fire risks associated with the EBS-H-5.3K lithium-ion battery? 2. How should we store EBS-H-5.3K batteries to prevent accidents? 3. Can we use a EBS-H-5.3K battery that was dropped or dented during transport? 4. Is it safe to perform welding work near an installed EBS-H-5.3K battery system? 5. What precautions are needed before moving or rewiring the EBS-H-5.3K battery system? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the battery safety requirements carefully. Do not expose batteries at high temperatures or around heat-generating sources, such as sunlight, fire sources, transformers and heaters. The battery may cause a fire if overheated. To avoid leakage, overheating or fire, do not disassemble, alter or damage batteries, do not insert foreign objects into batteries or place batteries in water or other liquids. The fire hazard of the lithium-ion battery energy storage system is high. Consider the following safety risks before handling batteries: Battery electrolytes can be combustible, toxic and volatile. Battery thermal runaway can generate flammable gas and harnnful gas such as CO and HF. The excessive concentration of flammable gas generated from battery thermal runaway may cause combustion and explosion. The batteries must be stored separately inside the packaging. Do not store batteries together with other materials or in the open air. Do not stack batteries too high. Do not use batteries beyond the warranty period. Do not remove the battery packaging before use. Batteries should be charged during storage by professionals as required. Put batteries back into their packagirng after charging during storage. Move batteries in the correct direction. Do not place a battery upside down or tilt it. Protect batteries from impact. Do not perform welding or grinding work around batteries to prevent fire caused by electric sparks or arcs. Use batteries within the temperature range specified in this manual. Do not use damaged batteries (such as damages caused when a battery is dropped, bumped or dented on the enclosure). Damaged batteries may release flammable gases. Do not store damaged batteries near undamaged products. Do not place damaged batteries in close proximity to flammable materials. Monitor damaged batteries during storage for signs of smoke, flammable electrolyte leakage, or heat. Do not move the battery system while the battery is operating. Including, but not limited to, when the circuit breaker and switch button are on, it is not allowed to move the BDU or modules, and it is also not allowed to plug and unplug the connector, otherwise there is a risk of electric shock. When the battery system is necessary to move or rewire, the power must be cut off.
1. Can u show me a schematic diagram of some label descriptions in EBS-H-5.3K battery safety requirements? | This is EBS-H-5.3K battery. The following link is a schematic diagram about some label descriptions in the battery safety requirements. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624112723040.jpg
1. What immediate actions should we take if the EBS-H-5.3K battery leaks electrolyte? 2. Can we use water to extinguish a EBS-H-5.3K battery fire? 3. What PPE is required for professionals handling a damaged EBS-H-5.3K battery? 4. Is it safe to reuse a EBS-H-5.3K battery after it’s dropped during installation? 5. How should firefighters approach a EBS-H-5.3K battery fire? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the emergency measures carefully. 1. Damaged Battery If the battery is damaged or flooded, it may leak the electrolyte and cause a short circuit fire. If the battery is wet or immersed in the water, do not try to touch it. If the battery seems to be damaged, they are not suitable for use and may be dangerous to personals or property. Avoid touching the leaked liquids or gases in the case of battery leakage or abnormal odor, do not approach the battery and contact professionals immediately. Professionals must wear safety goggles, rubber gloves, gas masks, and protective clothing. Electrolyte is corrosive and can cause irritation and chemical burns. In case of direct contact with the battery electrolyte, do as follows: > Inhalation: Evacuate contaminated areas, get fresh air immediately and seek immediate medical attention. > Eye contact: Immediately flush your eyes with water for at least 15 minutes, do not rub your eyes and seek medical attention immediately. > Skin contact: Wash the affected areas immediately with so and water and seek medical attention immediately. > Ingestion: Seek immediate medical assistance. 2. Battery Drop Emergency Measures If a battery is dropped or violently impacted during installaticon, internal damage may occur. Do not use such batteries. Otherwise, safety risks such as cell leakage and electric shock may arise. If a dropped battery has obvious damage or abnormal odor, snmoke or fire occurs, evacuate the personnel immediately, call emergency services, and contact professionals. Professionals can use fire extinguishing facilities to extinguish the fire under safety protection. If a dropped battery has no obvious deformation or damagee and no abnormal odor, smoke or fire occurs, contact professionals to transfer the battery to an open and safe place or contact a recycling company for disposal. 3. Fire Emergency Measures If a fire occurs, power off the system if it is safe to do so. Use carbon dioxide, FM-200 or ABC dry powder extinguishers to extinguish the fire. Ask firefighters to avoid contacting with high-voltage componeants during extinguishing fires to prevent the risk of electric shock. Overheating may cause batteries to deform and leak correosive electrolyte or toxic gas. Keep away from the batteries to avoid skin irritation and chemical burns.
1. How should we dispose of expired EBS-H-5.3K batteries? Can they be thrown in regular trash? 2. What should we do if a EBS-H-5.3K battery leaks or is physically damaged? 3. Who is authorized to handle EBS-H-5.3K battery recovery? | This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please follow the battery recovery process carefully. Dispose of used batteries in accordance with local laws and regulations. Do not dispose of batteries as household waste. If the batteries leak or are damaged, contact technical support or a battery recycling company for disposal. If the batteries are out of service life, contact a battery recyclinig company for disposal. Do not expose batteries to high temperatures or direct sunlight. Do not expose batteries to high humidity or corrosive environments.
This is EBS-H-5.3K battery. In order to prevent personal injury and property damage and ensure long-term operation of the battery system, please read the EU Declaration of Conformity carefully. The batteries sold on the European market by EnValt comply with the requirements of the following directives: Electromagnetic compatibility Directive 2014/30/EU (EMC) Electrical Apparatus Low Voltage Directive 2014/35/EU (LVD) Battery Directive 2006/66/EC and Amending Directive 2013/56/EU Waste Electrical and Electronic Equipment 2012/19/EU
1. What is the maximum charge/discharge current for the EBS-H-5.3K battery? 2. Does the EBS-H-5.3K support capacity expansion? 3. What battery chemistry does the EBS-H-5.3K battery use, and why? 4. Can the EBS-H-5.3K battery be controlled remotely? 5. Is professional installation required for the EBS-H-5.3K battery? | The EBS-H-5.3K is a new generation equipment with home energy storage system that can meet the diverse needs of global users. High-performance lithium iron phosphate battery is used for functional integration and modular structure design. It has realizedthe convenient expansion, rapid product installation, load matching, remote control and many other functions. Note: The nominal current of the EBS-H-5.3K product is 40 A. Please do not operate it under conditions exceeding this current. If the input or output current of the inverter connected to the battery exceeds 40 A, please use it in conjunction with the EnValt combiner box.
1. What are the main components of the EBS-H-5.3K battery system? 2. What safety features are integrated into the EBS-H-5.3K battery modules? 3. What is the function of the BDU (EBS-H-5.3K-EBDU)? 4. Why does the EBS-H-5.3K use lithium iron phosphate (LFP) chemistry? 5. Can the EBS-H-5.3K modules operate independently without the BDU? | This is EBS-H-5.3K battery. The battery system, which consists of a Battery Energy Distribution Unit (BDU for short), battery modules and a base, can store and release the electric energy according to the requirements of the solar energy storage system. 1. The Battery Energy Distribution Unit The Battery Energy Distribution Unit, EBS-H-5.3K-BDU, is connected to the total positive and negative electrodes of the battery module, and inside the BDU, there are communication firmware, Hall relays, resistors, and other parts to form a control circuit that is then connected to the power grid. 2. The battery modules Battery module, EBS-H-5.3K, consists of high-performaance lithium iron phosphate battery, fireproof module, aluminum extrusion end plate and other components, which is safe and reliable, and at the same time can be charged and discharged according to the load.
1. What's the definition of HOME-ESS-HV-15.9~63.6K battery system? | This is EBS-H-5.3K battery. The model of a battery system is HOME-ESS-HV-15.9~63.6K. The following link is a diagram of the battery system. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625163050867.png
1. What's the definition of EBS-H-5.3K-BDU? | This is EBS-H-5.3K battery. The model of a BDU is EBS-H-5.3K-BDU. The following link is a schematic diagram of definition of the BDU. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625163249250.png
1. What's the definition of EBS-H-5.3K battery module? | This is EBS-H-5.3K battery. The model of a battery module is EBS-H-5.3K. The following link is a schematic diagram of definition of battery module. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625163428221.png
1. What is the minimum and maximum number of EBS-H-5.3K battery modules supported in one system? 2. How many EBS-H-5.3K battery systems can be connected in parallel? 3. Where should the BDU be installed relative to EBS-H-5.3K battery modules? 4. Can I mix EBS-H-5.3K battery modules from different production batches? | This is EBS-H-5.3K battery. The battery system supports capacity expansion. The system can support capacity adjustment for a minimum of 3 and a maximum of 12 battery modules. The following link is a schematic diagram of EBS-H-5.3K battery system. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625163725925.png Note : Ensure that the BDU is installed above the battery modules. A max of 4 battery systems can be parallel connected in one energy storage system. The following link is a schematic diagram of energy storage system with 4 EBS-H-5.3K battery systems. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625163859769.png Note : Ensure that the usable energy of each battery system is the same.
1. Can u tell me some information about EBS-H-5.3K battery dimension drawings? | This is EBS-H-5.3K battery. The following link is a table of product dimesion and weight. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625164620139.png The following link is a schematic diagram of EBS-H-5.3K battery dimension drawings. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625164734410.png
1. Can u show me a schematic diagram of HOME-ESS-HV-3.7K battery's interface? | This is EBS-H-5.3K battery. Its interface consists of power switch, touch display, WiFi antenna, Fix screw, BDU, Battery module, Base, Breaker, Anti tipping bracket and grounding point. The following link is a schematic diagram of EBS-H-5.3K battery's interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625165037274.png
1. Can u tell me some product parameters about HOME-ESS-HV-3.7K battery? | This is HOME-ESS-HV-5.12K battery. The following link is a table of product parameters. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625165225580.png
1. What certifications are required to install the EBS-H-5.3K battery? 2. Can EBS-H-5.3K battery be installed outdoors in coastal areas? 3. What is the optimal operating temperature range for the EBS-H-5.3K battery? 4. Is EBS-H-5.3K battery wall-mountable or must it be ground-installed? 5. What clearance space is needed around EBS-H-5.3K battery for maintenance? | This is EBS-H-5.3K battery. Please read and understand this section carefully before installing the product! 1. Personnel Qualification Product installers should have received safety technical training, obtained the local electrician certifications and the authorized qualifications for product installation. And installers should be familiar with electrical equipment, accumulate relevant experience and have the following capabilities, including but not limited to: Setup, startup, shutdown, grounding, short-circuiting and repair ofelectrical equipment. Standardized maintenance and use of protective tools for electrical equipment. Providing emergency assistance for the injured. Complying with local laws, regulations, standards and directives. 2. Installation Environment Please make sure the installation location meets the following conditions: The building is designed to withstand earthquakes. The floor is flat and hard, and the area has minimal dust arnd dirt. The ambient environment is cool, dry, well-ventilated, and away from the sea, salt water, humid air, heat sources as well as direct sunlight. Temperature and humidity are kept at a constant level. There are no flammable and explosive items, corrosive gaases, including ammonia and acid vapors, and contaminants. Note: If the ambient temperature exceeds the operating range, the battery system will stop working to protect itself. The optimal temperature range for battery operation is 15°C to 35°C. Frequent exposure to inappropriate temperature may reduce battery performance and life. The following link is a schematic diagram of HOME-ESS-HV-5.12K battery installation environment. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625165401413.png 3. Installation Direction The battery system can be installed on the ground. Don't install the battery system at inclined, horizontal, or upside down positions. The following link is a schematic diagram of EBS-H-5.3K battery installation direction. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625133440637.png 4. Installation Space Leave enough space to install the battery system. InstallatioIn space is shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625165549711.png
1. What personal protective equipment (PPE) is mandatory for EBS-H-5.3K battery installation? 2. What tools are included vs. required for EBS-H-5.3K battery installation? 3. How do I verify if the EBS-H-5.3K battery shipment is complete? | This is EBS-H-5.3K battery. Here's some installation preparations. 1. Personal Protective Equipment The product is a household energy storage system. Impproper operation may cause personal injury and property damage. Personal protective tools must be used during installation. The following are the recommended personal protective tools: Safety gloves: Prevent the risk of electric shock and scratches during installation. Safety glasses: Prevent eye damage from splashing foreign objedcts during installation. Safety Shoes: Prevent the risk of electric shock. Ensure safety in case the module is accidentally dropped during installation. The following link is a schematic diagram of personal protective equipment in HOME-ESS-HV-5.12K battery installation. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625134145179.png 2. Installation Tools Tools needed in the process of installing equipment, more effective to improve installation efficiency. The following link is a schematic diagram of HOME-ESS-HV-5.12K battery installation tools. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625134308739.png 3. Open Box to Check Make sure the battery is intact during shipping. If there is any visible damage such as cracks, please contact your dealer immediately. Tear off the packaging tapes to unpack the battery. Ensure that the battery packaging and all related items are in good condition. Please check the packing list carefully by referring to Section 4.2.4 product accessories. If there's any item missing, please contact your dealer directly. The following link is a table of product accessories of HOME-ESS-HV-5.12K battery BDU. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625170035651.png The following link is a table of product accessories of EBS-H-5.3K battery modules. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625170111385.png
1. How to install EBS-H-5.3K battery? | This is EBS-H-5.3K battery. During its installation, pay attention to the following points. Make sure the ground is level and strong enough to bear the weight of products. Before you start connecting cables, make sure that the inverter and battery are entirely switched off! Make sure there is no water source above or near the battery, including downspouts, sprinklers, or faucets. The altitude to install the equipment shall be lower than the maximum working altitude 2000m. Install the equipment away from electromagnetic interference. If there is any radio or wireless communication device below 30MHz near the equipment, make sure that the equipment is at least 30m far away from the wireless device. Step 1: Locate drill holes in the wall Locating drill holes in the wall using the bracket 2(the longer)as a template with a level, position the holes on the wall, mark the positions of the 3 holes, and then drill 10mm holes to ensure that the depth of the holes exceeds 50mm. The bracket 2 should be placed (100+183*N)mm above the ground, (N=the number of the battery module). The following link is a schematic diagram of step 1. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625170513184.png Step 2: : Fix the anti tipping bracket 2 Fit the expansion tubes into the holes, pull them tight, and then use the expansion screws (packaged with expansion tube for use) to install and secure the wall mount bracket to the wall. The following link is a schematic diagram of step 2. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625170713556.png Step 3: Place the base Place the base along the wall with a recommended mounting distance of 30 mm between the base and the wall. The center hole of the bracket 2 is aligned with the cerhter of the base. The locking hole of the base is placed on the left. The following link is a schematic diagram of step 3. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625170900744.png Step 4: Install the anti tipping bracket 1 There are threaded holes on the back of the BDU. Using thhe M4x10 screws to install the anti tipping bracket 1 (the shorter) to it. The following link is a schematic diagram of step 4. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171050036.png Step 5: Install the battery Install the module and BDU in order from bottom to top. Make sure the locking holes of the anti-tipping bracket overlap from the side, if not, you need to re-adjust theposition of the battery to make it overlap. The following link is a schematic diagram of step 5. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171207581.png Step 6: Fix the battery modules Using the M4x10 screws to lock the bracket from both side ofthe BDU, and all the connectors on the right side between the BDU, module and base. The distance between the battery and the inverter should be no less than 400mm. The following link is a schematic diagram of step 6. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171332036.png Note: 1) High voltage products of different models cannot be mixed and stacked. High-voltage stacked modules must be of the same module with the same cell capacity and SOC. 2) With the exception of new battery modules that can be stacked directly for the first time, all other used batteries must be discharged to cutoff voltage or fully charged and meet capacity requirements before stacking.
1. Can u show me a schematic diagram of HOME-ESS-HV-3.7K battery BDU's interface? 2. What's the meaning of alphanumeric code on HOME-ESS-HV-3.7K battery BDU's connection interface? | This is EBS-H-5.3K battery. The following link is a schematic diagram of BDU's connection interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171709443.png The following link is a a diagram of definition of alphanumeric code on its BDU'S connection interface. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171902241.png The communication port pins are defined as follows: https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625171943428.png Before connecting the cables, use a multimeter to measure cable continuity, short circuits, and verify positive and negative terminals and cable labelling.
1. Can u show me a schematic diagram of electrical connections of a single EBS-H-5.3K battery system? 2. Can u show me a schematic diagram of electrical connections of parallel EBS-H-5.3K battery system? | This is EBS-H-5.3K battery. The electrical connections of a single battery system are shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625172235331.png The electrical connections of the parallel battery system are shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250625172857624.png
1. What's the use of black power cables of EBS-H-5.3K battery? 2. What's the use of red power cables of EBS-H-5.3K battery? 3. what's the use of CAN communication lines of EBS-H-5.3K battery? | This is EBS-H-5.3K battery. There are some preparing cables which can be listed as follows. 1. 6 mm² ground cable, used to ground the battery, should be prepared by the customer. 2. 1000mm black power cable 1, used to connect the negative pole between the battery system and the inverter, will be delivered with the product. 3. 1000mm red power cable 2, used to connect the positive pole between the battery system and the inverter, will be delivered with the product. 4. 1200mm black power cable 3, used to connect the negative pole between the battery systems, will be delivered with the product (Optional). 5. 1200mm red power cable 4, used to connect the positive pole between the battery systems, will be delivered with the product (Optional). 6. 1000mm CAN communication line 1, used to connect the communication interface between battery system and inverter, will be delivered with the product. 7. 1200mm CAN communication line 2, used to connect the communication interface between systems, will be delivered with the product (Optional). The following link is a diagram of these preparing cables of EBS-H-5.3K battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626090752310.png
1. How to do EBS-H-5.3K battery ground connection? | This is EBS-H-5.3K battery. Here are some steps of battery ground connection. 1) Crimp the ground terminal Customer needs to prepare the area for ground cable which shall be at least 4mm², then uses a ground screw and terminal to connect the ground cable. The bolt locking torque is 6NM. The following link is a schematic diagram of crimping method. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626091201384.png 2) Ground the battery with a ground wire through the ground screw and terminal. The following link is a schematic diagram of battery ground connection. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626091325456.png
1. Can u show me a schematic diagram of power connections between EBS-H-5.3K battery systems? | This is EBS-H-5.3K battery. When it comes to power connections between battery systems, use power cable 3 to connect the negative pole (P- terminal) of battery system A to the negative pole (P-terminal) of battery system B, and use power cable 4 to connect the positive pole (P+ terminal) of battery system A to the positive pole (P+terminal) of battery system B. For more than two battery system connections, connect the negative poles (P- terminal) between the battery systems and connect the positive poles (P+ terminal) between the battery systems. The following link is a schematic diagram of power connections between EBS-H-5.3K battery systems. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626091633314.png
1. How to do power cable connections between EBS-H-5.3K battery system and inverter? | This is EBS-H-5.3K battery. When it comes to power cable connections between the battery system and inverter, after the battery system is connected, connect the negative pole(P- terminal) of the battery system A and the BAT - terminal of the inverter with the power cable 1; connect tlhe positive pole (P+ terminal) of the battery system A and the BAT + terminal of the inverter with the power cable 2. The following link is a schematic diagram of power cable connections between EBS-H-5.3K battery system and inverter. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626091927775.png Note: Before the inverter is connected to power cable, the inverter and battery systems need to be powered off. It is forbidden to mix batteries of different brands, specifications and batches, otherwise it will cause system failure.
1. How to do communication connection of EBS-H-5.3K battery? | This is EBS-H-5.3K battery. When it comes to communication connection, 1. Use the CAN communication cable 1 to connect the inverter with the primary through CAN protocol. The following link is a schematic diagram of how to connect the CAN communication cable 1 of EBS-H-5.3K battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626092205938.png 2. Use the CAN communication cable 2 to connect the battery sysstem in sequence through the CAN protocol. The following link is a schematic diagram of how to connect the CAN communication cable 2 of EBS-H-5.3K battery. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626092255141.png Note: The communication between the inverter and the battery system must be made with CAN communication lines connected to the PCS port of the BDU, otherwise communication cannot be performed; the communication between the clusters must be made with CAN communication lines connected to the BAT-IN and BAT-OUT port.
1. What happens if slave cluster BDUs are powered on before the main BDU in EBS-H-5.3K battery? 2. How does the main BDU assign addresses to slave clusters in EBS-H-5.3K battery? 3. Why must circuit breakers be toggled before battery power switches in EBS-H-5.3K battery? 4. What indications confirm successful networking of battery clusters in EBS-H-5.3K battery? 5. Can a slave cluster be hot-swapped without shutting down EBS-H-5.3K battery? | This is EBS-H-5.3K battery. Here is equipment debugging. 1. Equipment Power on 1) Confirm again that the cables are connected in the correct order and the connection is firm before starting. 2) Then toggle the circuit breaker on the main battery pack BDU to ON and observe the status on the display to ensure that the main battery cluster is normal. (The battery cluster connected to the inverter for CAN communication is the main battery cluster). 3) Then toggle the circuit breakers on the slave cluster BDUs to ON in sequence and observe the status on the display to ensure that the slave cluster status is normal. The master cluster BDU will automatically recognize the number of battery clusters in parallel connection and assign addresses. The one connected to the inverter is the main cluster and the remaining parallel clusters are slave clusters 1, 2 and 3. 4) After the display shows successful networking, press the power switch for each battery cluster in sequence. NOTE: When the system starts, ensure the boot sequence of each equipment, otherwise it may cause pre-charging and the circuit breaker protection fault.
1. How to resolve registration failure in EnValtESS app for EBS-H-5.3K battery? 2. Why can’t I create/add devices to a station in EnValtESS with EBS-H-5.3K battery? 3. What if the EBS-H-5.3K battery fails to connect to Wi-Fi via its display? 4. Why doesn’t the EBS-H-5.3K battery appear in device search after going online? 5. How to troubleshoot missing inverter protocol options in EnValtESS for EBS-H-5.3K battery? | This is EBS-H-5.3K battery. Here is equipment debugging. 2. Application Connections Please download the EnValtESS app by scanning the QR code or frorn the APP Store. Step 1: Register and login Tap "Sign up" and fill in the information, then tap "Confirm" to login. If you have already registered, you can tap "Sign in" directly as shown in the schematic diagram in the following link. https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/20250626093303405.png Step 2: Create station Tap "Create station" on the page and fill in information for the new station, as shown in the schematic diagram in the following link. https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/20250626093406263.png If you already have a station, still need to add new devices to your station. Please tap the "+" button to add devices to your station, as shown in the schematic diagram in the following link. https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/20250626093455456.png Step 3: Batteries on line Click on the WIFI menu on the battery display, select the WiFi network you want to connect to, enter the WiFi password and bring the battery system online. Step 4: Device search After the battery is successfully online, you can search for tthe battery in this interface as shown in the schematic diagram in the following link. https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/20250626093635900.png Step 5: Enjoy smart energy After completing the above steps, you can view the battery data in EnValtESS app, upgrade the battery online, select the inverter protocol as shown in the schematic diagram in the following link https://oss-cdn.EnValtess.com//Knowledge_data_base/user_manual/20250626093804565.png ,and more smart functions are waiting for you to discover.
1. How to confirm inverter-supported protocols for EBS-H-5.3K battery compatibility? 2. Why does the EBS-H-5.3K battery default protocol (EnValt) cause inverter communication failure? 3. What if the required inverter protocol isn’t listed in EnValtESS app for EBS-H-5.3K battery? 4. How to verify protocol synchronization between EBS-H-5.3K battery and inverter? 5. Why doesn’t the inverter display EBS-H-5.3K battery data after protocol selection? | This is EBS-H-5.3K battery. Here is equipment debugging. 3. Inverter Protocol Selection The battery system default factory CAN communication is EnValt protocol. Protocol Selection: 1) Check which protocols the inverter supports. 2) If the inverter supports the battery factory default protocol, select the corresponding protocol directly on the inverter. 3) If the inverter supports protocols other than the battery factory default protocol, select the same protocol on the battery system and the inverter. Battery system protocol selection: Select the interface and communication protocol that matches the inverter on the APP of the battery (protocol options include ENVALT, Pyvlon, Luxpower, SOFARSOLAR), see 4.6.2 for the APP selection method. After the setting is completed, you can see the normal status information of the battery system from the inverter, such as voltage, SOC .
1. What happens if the inverter isn't turned off before powering down EBS-H-5.3K battery clusters? 2. Why must slave battery clusters be powered off before the master in EBS-H-5.3K battery? 3. What occurs if BDU circuit breakers are shut down out of sequence (e.g., slave before master) in EBS-H-5.3K battery? 4. How to confirm all EBS-H-5.3K battery components are safely de-energized after shutdown? 5. What errors occur if protocol settings aren’t preserved during EBS-H-5.3K battery power-down? | This is EBS-H-5.3K battery. Here is equipment debugging. 4. Equipment Power Down 1) First, turn off the inverter. 2) Turn off the power switch of the salve battery cluster and the master battery cluster in turn. 3) Turn off the circuit breaker switch on the BDU in the order of Mdaster Battery Cluster, Slave Battery Cluster 1, Slave Battery Cluster 2 and Slave Battery Cluster 3.
1. Why does the EBS-H-5.3K battery display show no homepage after BDU power-on? 2. Why does the EBS-H-5.3K battery display show positive current during system discharging? 3. Why does the EBS-H-5.3K battery display fail to show voltage/SOC/temperature after startup? 4. Why does the EBS-H-5.3K battery display show incorrect current values during charging? 5. Why does the EBS-H-5.3K battery display show abnormal values despite successful power-on? | This is EBS-H-5.3K battery. After the stacking installation is completed, turn on the circuit breaker on the BDU and the display will show its home page in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626094806395.png The main page of the display can show common operating status data such as voltage, SOC, temperature, charge/discharge current. NOTE: The current data will shown in the schematic diagram in the following link https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626094806395.png when thhe system is charging, and as negative when the system is discharging.
1. Why can’t the battery system name/SN code/factory date be viewed when touching the "Information" option on the EBS-H-5.3K battery display? 2. Why does the EBS-H-5.3K battery display fail to show the Wi-Fi signal icon after completing Wi-Fi setup? 3. Why can’t remote upgrades for BCU/Wi-Fi module/LCD be performed via the "OTA" option on the EBS-H-5.3K battery? 4. Why does the "Alarm" option on the EBS-H-5.3K battery display fail to show current faults or recent operation problems? 5. Why can’t force charging be activated via the display when cell voltage is too low on the EBS-H-5.3K battery? | This is EBS-H-5.3K battery. Interactive function icons are located below the battery display. 1. Information Touch the "Information" option in the menu bar. You can view the battery system name, SN code, factory date, number of stacked modules, battery capacity and other inforrmation. 2. WIFI Touch the "WIFI" option in the menu bar, the display is shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626095845211.png Click the drop-down menu to select the WiFi you want to connect to, enter the password and click Confirm. When the connection is successful, a WiFi signal appears at the top of the home page of the display. 3. OTA Touch the "OTA" option in the menu bar, the display is shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626100012938.png In this interface, you can choose to upgrade BCU version, WIFI module version and LCD versionto the latest version remotely. NOTE: Upgradation requires network. 4. Alarm Touch the "Alarm" option in the menu bar, the display is shown in the schematic diagram in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250626100211837.png This feature displays current system faults and also allows you to read and view problems that have occurred in the recent operation of the battery system. 5. Force Charge Forced charging of batteries by skipping program settings insome cases. For example, charging can be forced when the cell voltage is too low.
1. What're EBS-H-5.3K battery environment requirements? | This is EBS-H-5.3K battery. Here's some battery storage information. The battery is required to be stored in a temperature range from O°C to +40°C. Routine maintenance is required for batteries that have been stored for a long time. Depending on the storage time of the battery and the storage environment, Please charge the battery to the corresponding SOC at 0.2C as required by the table below in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100014207.png After a long-time storage, the battery should be inspected and tested by professionals before use. During the storage period, record temperature, humidity and storage environment in accordance with storage requirements in this manual. Long-term storage of batteries is not recommended, which will cause capacity loss. Generally, after 12 months of storage at the recommended storage temperature, an irreversible capacity loss of lithium batteries is 3%~10%. The batteries should be stored in accordance with the labels on the packaging box and should not be inverted or placed sideways. The battery boxes should be stacked according to the stacking requirements on the outer packaging. When handling the battery, take care not to damage the battery. Storage Environment Requirements: Ambient temperature: short-term storage (less than 1 month)O°C~~40°C, long-term storage (more than 1 month)5°C~35°C. Recommended storage temperature: 20°C~30°C. Relative humidity: 5%RH~60%RH. Store products in a dry, clean and ventilated place. Keep them away from dust, direct sunlight, rain, vapor or groundwater. Avoid contact with corrosive organic solvents, gases and other substances.
1. What're EBS-H-5.3K battery charging requirements after over-discharge? | This is EBS-H-5.3K battery. Here're some charging requirements after over-discharge. The battery stops discharging there is still static power consumpttion of the internal battery module and its own self-discharge loss, if there is no charge for a long time to replenish, it may lead to battery damage due to over-discharge. When the battery SOC is low, it needs to be replenished according to the maximum interval in the table in the following link. https://oss-cdn.hanchuess.com//Knowledge_data_base/user_manual/20250624100543031.png We do not provide warranty service for permanent battery failure due to overdue recharging by the customer.
1. Can u give me some long-term idle maintenance requirements for EBS-H-5.3K battery? | This is EBS-H-5.3K battery. Here are some long-term idle maintenance requirements. If a long period of inactivity (≥30 days) is planned, the following two requirements should be observed to protect the battery: 1) Ensure that the battery's SOC system is above 30% and that the battery circuit breaker and power switch remain off. 2) If it is stored for more than 30 days, due to different temperature and different storage time, it has different effects on self-discharge. Therefore, before the battery batteries go online, it is necessary to check the voltage completely to confirm the necessity of maintainirg the state of charge, our company can assist the customer to make a judgment. 3) If the interval between two charges of the battery exceeds 2 months, the standard charging mode should be adopted for 2~3 times before the battery performance can reeach the best state. 4) If it is stored for more than 3 months, it shall be tested and maintained every 3 months. If it is not tested or maintained for more than 9 months, EnValt will not be resporasible for quality protection for capacity loss or other defects caused by batteries. Note: We do not provide appropriate warranty service forpermanent battery failure due to improper storage by the customer.
1. Can u give me some EBS-H-5.3K battery maintenance safety requirements? | This is EBS-H-5.3K battery. Here are some battery maintenance safety requirements. When the equipment is running, a high voltage may cause electric shocks and result in death, serious injury or property damage. Before performing maintenance, turn off the equipment and strictly follow the safety precautions listed in this manual and other related documents. Ensure that you are familiar with the contents of this manual and have appropriate tools and test equipment to perform maintenance. Before performing maintenance, turn off the equipment according to the instructions and wait for a certain period of time to ensure that the equipment is power-off. During maintenance, prevent unnecessary personnel from getting close to the maintenance site. Temporary warning signs or fences must be erected to isolate the site. If the equipment fails, please contact your dealer in time to deal with it. The equipment can only be power-on again after the fault has been dealt with. Otherwise, the equipment may have some problems or become damaged. Do not dissemble the product without authorization. There is a danger of electric shocks and the corresponding failure is not covered by the warranty. Maintenance personnel should have received the professional training and use protective tools to conduct maintenance. When it is necessary to move or rewire, the input power must be cut off. Wait for 5 minutes to ensure that the internal energy of the machine has been discharged. The maintenance should be started after confirming with a multimeter that there is no dangerous voltage and no parts need to be repaired inside the machine. Maintenance of batteries should be performed or supervised by someone who is familiar with batteries and required precautions. Please use the same type of cell when replacing cells. After maintenance, immediately check that no tools or other parts have been left inside the equipment. If the equipment has not been used for a long time, you need to store and charge the battery according to this manual. All operators of the energy storage system shall comply with the user manual. Any equipment damage caused by neglecting or misreading the user manual, will void the product warranty.